## Rev04
No. | Device |  | Name | Description | I/O Type | IP address =? Port = 502? Slave ID = ? | Modbus Address | Data Type (16 bit Int / Boolean?) | Query Response time (sec) | Location | Qty | Remarks
Terasaki
1 | 12 | D/G#1 | Over Speed | On overspeed [806.4min-1(112%), 828 min-1(115%)] | Digital |  |  |  | 0.5 | GCP#1 | 1 |  | Engine Trip
| 12 | D/G#2 | Over Speed | On overspeed [806.4min-1(112%), 828 min-1(115%)] | Digital |  |  |  | 0.5 | GCP#2 | 1 |  | Engine Trip
| 12 | D/G#3 | Over Speed | On overspeed [806.4min-1(112%), 828 min-1(115%)] | Digital |  |  |  | 0.5 | GCP#3 | 1 |  | Engine Trip
| 12 | D/G#4 | Over Speed | On overspeed [806.4min-1(112%), 828 min-1(115%)] | Digital |  |  |  | 0.5 | GCP#4 | 1 |  | Engine Trip
2 | 48T | D/G#1 | Engine Start Failure | IN CASE OF (14) KEEPING-OFF AFTER 20 Sec FROM (88V) ACTIVATION | Digital |  |  |  | 0.5 | GCP#1 | 1
| 48T | D/G#2 | Engine Start Failure | IN CASE OF (14) KEEPING-OFF AFTER 20 Sec FROM (88V) ACTIVATION | Digital |  |  |  | 0.5 | GCP#2 | 1
| 48T | D/G#3 | Engine Start Failure | IN CASE OF (14) KEEPING-OFF AFTER 20 Sec FROM (88V) ACTIVATION | Digital |  |  |  | 0.5 | GCP#3 | 1
| 48T | D/G#4 | Engine Start Failure | IN CASE OF (14) KEEPING-OFF AFTER 20 Sec FROM (88V) ACTIVATION | Digital |  |  |  | 0.5 | GCP#4 | 1
3 | 26EX2 | D/G#1 | Turbo-charger gas outlet temp switch (2nd) | On over 430°C | Digital |  |  |  | 0.5 | GCP#1 | 1 |  | As per "TCTO"(T/C outlet Temp), Engine Trip
| 26EX2 | D/G#2 | Turbo-charger gas outlet temp switch (2nd) | On over 430°C | Digital |  |  |  | 0.5 | GCP#2 | 1 |  | As per "TCTO"(T/C outlet Temp), Engine Trip
| 26EX2 | D/G#3 | Turbo-charger gas outlet temp switch (2nd) | On over 430°C | Digital |  |  |  | 0.5 | GCP#3 | 1 |  | As per "TCTO"(T/C outlet Temp), Engine Trip
| 26EX2 | D/G#4 | Turbo-charger gas outlet temp switch (2nd) | On over 430°C | Digital |  |  |  | 0.5 | GCP#4 | 1 |  | As per "TCTO"(T/C outlet Temp), Engine Trip
4 | MDHH | D/G#1 | Heavy fault of oil mist detector | ON WHEN OIL MIST LEVEL RED: "15" | Digital |  |  |  | 0.5 | GCP#1 | 1
| MDHH | D/G#2 | Heavy fault of oil mist detector | ON WHEN OIL MIST LEVEL RED: "15" | Digital |  |  |  | 0.5 | GCP#2 | 1
| MDHH | D/G#3 | Heavy fault of oil mist detector | ON WHEN OIL MIST LEVEL RED: "15" | Digital |  |  |  | 0.5 | GCP#3 | 1
| MDHH | D/G#4 | Heavy fault of oil mist detector | ON WHEN OIL MIST LEVEL RED: "15" | Digital |  |  |  | 0.5 | GCP#4 | 1
5 | 63Q2 | D/G#1 | L.O press.switch for engine (2nd) | ON BELOW 0.3MPa | Digital |  |  |  | 0.5 | GCP#1 | 1 |  | Engine Trip
| 63Q2 | D/G#2 | L.O press.switch for engine (2nd) | ON BELOW 0.3MPa | Digital |  |  |  | 0.5 | GCP#2 | 1 |  | Engine Trip
| 63Q2 | D/G#3 | L.O press.switch for engine (2nd) | ON BELOW 0.3MPa | Digital |  |  |  | 0.5 | GCP#3 | 1 |  | Engine Trip
| 63Q2 | D/G#4 | L.O press.switch for engine (2nd) | ON BELOW 0.3MPa | Digital |  |  |  | 0.5 | GCP#4 | 1 |  | Engine Trip
6 | 26WJ2 | D/G#1 | Jacket water thermal switch (2nd) | ON OVER 90°C | Digital |  |  |  | 0.5 | GCP#1 | 1 |  | Engine Trip
| 26WJ2 | D/G#2 | Jacket water thermal switch (2nd) | ON OVER 90°C | Digital |  |  |  | 0.5 | GCP#2 | 1 |  | Engine Trip
| 26WJ2 | D/G#3 | Jacket water thermal switch (2nd) | ON OVER 90°C | Digital |  |  |  | 0.5 | GCP#3 | 1 |  | Engine Trip
| 26WJ2 | D/G#4 | Jacket water thermal switch (2nd) | ON OVER 90°C | Digital |  |  |  | 0.5 | GCP#4 | 1 |  | Engine Trip
7 | 63QT2 | D/G#1 | L.O press.switch for turbo-charger(2nd) | ON BELOW 0.20MPa | Digital |  |  |  | 0.5 | GCP#1 | 1 |  | Engine Trip
| 63QT2 | D/G#2 | L.O press.switch for turbo-charger(2nd) | ON BELOW 0.20MPa | Digital |  |  |  | 0.5 | GCP#2 | 1 |  | Engine Trip
| 63QT2 | D/G#3 | L.O press.switch for turbo-charger(2nd) | ON BELOW 0.20MPa | Digital |  |  |  | 0.5 | GCP#3 | 1 |  | Engine Trip
| 63QT2 | D/G#4 | L.O press.switch for turbo-charger(2nd) | ON BELOW 0.20MPa | Digital |  |  |  | 0.5 | GCP#4 | 1 |  | Engine Trip
8 | 63WJ2 | D/G#1 | Jacket water press.switch (2nd) | ON BELOW 0.1MPa | Digital |  |  |  | 0.5 | GCP#1 | 1 |  | Engine Trip
| 63WJ2 | D/G#2 | Jacket water press.switch (2nd) | ON BELOW 0.1MPa | Digital |  |  |  | 0.5 | GCP#2 | 1 |  | Engine Trip
| 63WJ2 | D/G#3 | Jacket water press.switch (2nd) | ON BELOW 0.1MPa | Digital |  |  |  | 0.5 | GCP#3 | 1 |  | Engine Trip
| 63WJ2 | D/G#4 | Jacket water press.switch (2nd) | ON BELOW 0.1MPa | Digital |  |  |  | 0.5 | GCP#4 | 1 |  | Engine Trip
9 |  | D/G#1 | DC control power supply failure |  | Digital |  |  |  | 0.5 | GCP#1 | 1
|  | D/G#2 | DC control power supply failure |  | Digital |  |  |  | 0.5 | GCP#2 | 1
|  | D/G#3 | DC control power supply failure |  | Digital |  |  |  | 0.5 | GCP#3 | 1
|  | D/G#4 | DC control power supply failure |  | Digital |  |  |  | 0.5 | GCP#4 | 1
10 |  | D/G#1 | GAC Abnormal |  | Digital |  |  |  | 0.5 | GCP#1 | 1
|  | D/G#2 | GAC Abnormal |  | Digital |  |  |  | 0.5 | GCP#2 | 1
|  | D/G#3 | GAC Abnormal |  | Digital |  |  |  | 0.5 | GCP#3 | 1
|  | D/G#4 | GAC Abnormal |  | Digital |  |  |  | 0.5 | GCP#4 | 1
11 | 5E | D/G#1 | Emergency stop |  | Digital |  |  |  | 0.5 | GCP#1 | 1 |  | To consider from drums a dry contact to GCP; purpose for the client to activate stop engine/open cb remotely
| 5E | D/G#2 | Emergency stop |  | Digital |  |  |  | 0.5 | GCP#2 | 1 |  | To consider from drums a dry contact to GCP; purpose for the client to activate stop engine/open cb remotely
| 5E | D/G#3 | Emergency stop |  | Digital |  |  |  | 0.5 | GCP#3 | 1 |  | To consider from drums a dry contact to GCP; purpose for the client to activate stop engine/open cb remotely
| 5E | D/G#4 | Emergency stop |  | Digital |  |  |  | 0.5 | GCP#4 | 1 |  | To consider from drums a dry contact to GCP; purpose for the client to activate stop engine/open cb remotely
12 | 69WJ | D/G#1 | Jacket water flow relay | ON BELOW 40m³/h | Digital |  |  |  | 0.5 | GCP#1 | 1 |  | Timer 10 Sec
| 69WJ | D/G#2 | Jacket water flow relay | ON BELOW 40m³/h | Digital |  |  |  | 0.5 | GCP#2 | 1 |  | Timer 10 Sec
| 69WJ | D/G#3 | Jacket water flow relay | ON BELOW 40m³/h | Digital |  |  |  | 0.5 | GCP#3 | 1 |  | Timer 10 Sec
| 69WJ | D/G#4 | Jacket water flow relay | ON BELOW 40m³/h | Digital |  |  |  | 0.5 | GCP#4 | 1 |  | Timer 10 Sec
13 |  | D/G#1 | Over voltage |  | Digital |  |  |  | 0.5 | GCP#1 | 1
|  | D/G#2 | Over voltage |  | Digital |  |  |  | 0.5 | GCP#2 | 1
|  | D/G#3 | Over voltage |  | Digital |  |  |  | 0.5 | GCP#3 | 1
|  | D/G#4 | Over voltage |  | Digital |  |  |  | 0.5 | GCP#4 | 1
14 |  | D/G#1 | Under voltage |  | Digital |  |  |  | 0.5 | GCP#1 | 1
|  | D/G#2 | Under voltage |  | Digital |  |  |  | 0.5 | GCP#2 | 1
|  | D/G#3 | Under voltage |  | Digital |  |  |  | 0.5 | GCP#3 | 1
|  | D/G#4 | Under voltage |  | Digital |  |  |  | 0.5 | GCP#4 | 1
15 |  | D/G#1 | Gen differential |  | Digital |  |  |  | 0.5 | GCP#1 | 1
|  | D/G#2 | Gen differential |  | Digital |  |  |  | 0.5 | GCP#2 | 1
|  | D/G#3 | Gen differential |  | Digital |  |  |  | 0.5 | GCP#3 | 1
|  | D/G#4 | Gen differential |  | Digital |  |  |  | 0.5 | GCP#4 | 1
16 |  | D/G#1 | Reverse power |  | Digital |  |  |  | 0.5 | GCP#1 | 1
|  | D/G#2 | Reverse power |  | Digital |  |  |  | 0.5 | GCP#2 | 1
|  | D/G#3 | Reverse power |  | Digital |  |  |  | 0.5 | GCP#3 | 1
|  | D/G#4 | Reverse power |  | Digital |  |  |  | 0.5 | GCP#4 | 1
17 |  | D/G#1 | Field failure |  | Digital |  |  |  | 0.5 | GCP#1 | 1
|  | D/G#2 | Field failure |  | Digital |  |  |  | 0.5 | GCP#2 | 1
|  | D/G#3 | Field failure |  | Digital |  |  |  | 0.5 | GCP#3 | 1
|  | D/G#4 | Field failure |  | Digital |  |  |  | 0.5 | GCP#4 | 1
18 | MDH | D/G#1 | Light fault of oil mist detector | ON WHEN OIL MIST LEVEL RED: "10" | Digital |  |  |  | 0.5 | GCP#1 | 1
| MDH | D/G#2 | Light fault of oil mist detector | ON WHEN OIL MIST LEVEL RED: "10" | Digital |  |  |  | 0.5 | GCP#2 | 1
| MDH | D/G#3 | Light fault of oil mist detector | ON WHEN OIL MIST LEVEL RED: "10" | Digital |  |  |  | 0.5 | GCP#3 | 1
| MDH | D/G#4 | Light fault of oil mist detector | ON WHEN OIL MIST LEVEL RED: "10" | Digital |  |  |  | 0.5 | GCP#4 | 1
19 | MDSY | D/G#1 | Light fault of oil mist detector system failure | ON WHEN SYSTEM FAILURE OCCURS | Digital |  |  |  | 0.5 | GCP#1 | 1
| MDSY | D/G#2 | Light fault of oil mist detector system failure | ON WHEN SYSTEM FAILURE OCCURS | Digital |  |  |  | 0.5 | GCP#2 | 1
| MDSY | D/G#3 | Light fault of oil mist detector system failure | ON WHEN SYSTEM FAILURE OCCURS | Digital |  |  |  | 0.5 | GCP#3 | 1
| MDSY | D/G#4 | Light fault of oil mist detector system failure | ON WHEN SYSTEM FAILURE OCCURS | Digital |  |  |  | 0.5 | GCP#4 | 1
20 | 63Q1 | D/G#1 | LO press.switch for engine(1st) | ON BELOW 0.35MPa | Digital |  |  |  | 0.5 | GCP#1 | 1 |  | As per "PTLO"
| 63Q1 | D/G#2 | LO press.switch for engine(1st) | ON BELOW 0.35MPa | Digital |  |  |  | 0.5 | GCP#2 | 1 |  | As per "PTLO"
| 63Q1 | D/G#3 | LO press.switch for engine(1st) | ON BELOW 0.35MPa | Digital |  |  |  | 0.5 | GCP#3 | 1 |  | As per "PTLO"
| 63Q1 | D/G#4 | LO press.switch for engine(1st) | ON BELOW 0.35MPa | Digital |  |  |  | 0.5 | GCP#4 | 1 |  | As per "PTLO"
21 | 63QP | D/G#1 | LO press.switch for priming | ON OVER 0.03MPa | Digital |  |  |  | 0.5 | GCP#1 | 1 |  | NO PRESS. AFTER 60-90sec. FROM PUMP START
| 63QP | D/G#2 | LO press.switch for priming | ON OVER 0.03MPa | Digital |  |  |  | 0.5 | GCP#2 | 1 |  | NO PRESS. AFTER 60-90sec. FROM PUMP START
| 63QP | D/G#3 | LO press.switch for priming | ON OVER 0.03MPa | Digital |  |  |  | 0.5 | GCP#3 | 1 |  | NO PRESS. AFTER 60-90sec. FROM PUMP START
| 63QP | D/G#4 | LO press.switch for priming | ON OVER 0.03MPa | Digital |  |  |  | 0.5 | GCP#4 | 1 |  | NO PRESS. AFTER 60-90sec. FROM PUMP START
22 | 63WC | D/G#1 | Cooler water press switch | ON BELOW 0.1MPa | Digital |  |  |  | 0.5 | GCP#1 | 1 |  | As per "PTCW"
| 63WC | D/G#2 | Cooler water press switch | ON BELOW 0.1MPa | Digital |  |  |  | 0.5 | GCP#2 | 1 |  | As per "PTCW"
| 63WC | D/G#3 | Cooler water press switch | ON BELOW 0.1MPa | Digital |  |  |  | 0.5 | GCP#3 | 1 |  | As per "PTCW"
| 63WC | D/G#4 | Cooler water press switch | ON BELOW 0.1MPa | Digital |  |  |  | 0.5 | GCP#4 | 1 |  | As per "PTCW"
23 | 63QT1 | D/G#1 | L.O. press switch for turbo-charger (1st) | ON BELOW 0.25MPa | Digital |  |  |  | 0.5 | GCP#1 | 1 |  | As per "PTTLO"
| 63QT1 | D/G#2 | L.O. press switch for turbo-charger (1st) | ON BELOW 0.25MPa | Digital |  |  |  | 0.5 | GCP#2 | 1 |  | As per "PTTLO"
| 63QT1 | D/G#3 | L.O. press switch for turbo-charger (1st) | ON BELOW 0.25MPa | Digital |  |  |  | 0.5 | GCP#3 | 1 |  | As per "PTTLO"
| 63QT1 | D/G#4 | L.O. press switch for turbo-charger (1st) | ON BELOW 0.25MPa | Digital |  |  |  | 0.5 | GCP#4 | 1 |  | As per "PTTLO"
24 | 26WJ1 | D/G#1 | Jacket water thermal switch (1st) | ON OVER 85°C | Digital |  |  |  | 0.5 | GCP#1 | 1 |  | As per "TRJWO"
| 26WJ1 | D/G#2 | Jacket water thermal switch (1st) | ON OVER 85°C | Digital |  |  |  | 0.5 | GCP#2 | 1 |  | As per "TRJWO"
| 26WJ1 | D/G#3 | Jacket water thermal switch (1st) | ON OVER 85°C | Digital |  |  |  | 0.5 | GCP#3 | 1 |  | As per "TRJWO"
| 26WJ1 | D/G#4 | Jacket water thermal switch (1st) | ON OVER 85°C | Digital |  |  |  | 0.5 | GCP#4 | 1 |  | As per "TRJWO"
25 | 26WC | D/G#1 | Cooler water thermal switch | ON OVER 50°C | Digital |  |  |  | 0.5 | GCP#1 | 1
| 26WC | D/G#2 | Cooler water thermal switch | ON OVER 50°C | Digital |  |  |  | 0.5 | GCP#2 | 1
| 26WC | D/G#3 | Cooler water thermal switch | ON OVER 50°C | Digital |  |  |  | 0.5 | GCP#3 | 1
| 26WC | D/G#4 | Cooler water thermal switch | ON OVER 50°C | Digital |  |  |  | 0.5 | GCP#4 | 1
26 | 26Q | D/G#1 | L.O. thermal switch | ON OVER 65°C | Digital |  |  |  | 0.5 | GCP#1 | 1
| 26Q | D/G#2 | L.O. thermal switch | ON OVER 65°C | Digital |  |  |  | 0.5 | GCP#2 | 1
| 26Q | D/G#3 | L.O. thermal switch | ON OVER 65°C | Digital |  |  |  | 0.5 | GCP#3 | 1
| 26Q | D/G#4 | L.O. thermal switch | ON OVER 65°C | Digital |  |  |  | 0.5 | GCP#4 | 1
27 | 33QSL | D/G#1 | L.O. sump tank level switch | ON BELOW LOWER LIMIT | Digital |  |  |  | 0.5 | GCP#1 | 1 |  | Timer 5 sec
| 33QSL | D/G#2 | L.O. sump tank level switch | ON BELOW LOWER LIMIT | Digital |  |  |  | 0.5 | GCP#2 | 1 |  | Timer 5 sec
| 33QSL | D/G#3 | L.O. sump tank level switch | ON BELOW LOWER LIMIT | Digital |  |  |  | 0.5 | GCP#3 | 1 |  | Timer 5 sec
| 33QSL | D/G#4 | L.O. sump tank level switch | ON BELOW LOWER LIMIT | Digital |  |  |  | 0.5 | GCP#4 | 1 |  | Timer 5 sec
28 | 63WJ1 | D/G#1 | Jacket water press switch (1st) | ON BELOW 0.15MPa | Digital |  |  |  | 0.5 | GCP#1 | 1 |  | As per "PTJW"
| 63WJ1 | D/G#2 | Jacket water press switch (1st) | ON BELOW 0.15MPa | Digital |  |  |  | 0.5 | GCP#2 | 1 |  | As per "PTJW"
| 63WJ1 | D/G#3 | Jacket water press switch (1st) | ON BELOW 0.15MPa | Digital |  |  |  | 0.5 | GCP#3 | 1 |  | As per "PTJW"
| 63WJ1 | D/G#4 | Jacket water press switch (1st) | ON BELOW 0.15MPa | Digital |  |  |  | 0.5 | GCP#4 | 1 |  | As per "PTJW"
29 | 63QD | D/G#1 | L.O. filter differential press switch | ON OVER 0.09MPa | Digital |  |  |  | 0.5 | GCP#1 | 1
| 63QD | D/G#2 | L.O. filter differential press switch | ON OVER 0.09MPa | Digital |  |  |  | 0.5 | GCP#2 | 1
| 63QD | D/G#3 | L.O. filter differential press switch | ON OVER 0.09MPa | Digital |  |  |  | 0.5 | GCP#3 | 1
| 63QD | D/G#4 | L.O. filter differential press switch | ON OVER 0.09MPa | Digital |  |  |  | 0.5 | GCP#4 | 1
30 | 63QTD | D/G#1 | T/C L.O filter differential press switch | ON OVER 0.06MPa | Digital |  |  |  | 0.5 | GCP#1 | 1
| 63QTD | D/G#2 | T/C L.O filter differential press switch | ON OVER 0.06MPa | Digital |  |  |  | 0.5 | GCP#2 | 1
| 63QTD | D/G#3 | T/C L.O filter differential press switch | ON OVER 0.06MPa | Digital |  |  |  | 0.5 | GCP#3 | 1
| 63QTD | D/G#4 | T/C L.O filter differential press switch | ON OVER 0.06MPa | Digital |  |  |  | 0.5 | GCP#4 | 1
31 | 33HF | D/G#1 | F.O leak tank level switch | ON OVER UPPER LIMIT | Digital |  |  |  | 0.5 | GCP#1 | 1 |  | Timer 5 sec
| 33HF | D/G#2 | F.O leak tank level switch | ON OVER UPPER LIMIT | Digital |  |  |  | 0.5 | GCP#2 | 1 |  | Timer 5 sec
| 33HF | D/G#3 | F.O leak tank level switch | ON OVER UPPER LIMIT | Digital |  |  |  | 0.5 | GCP#3 | 1 |  | Timer 5 sec
| 33HF | D/G#4 | F.O leak tank level switch | ON OVER UPPER LIMIT | Digital |  |  |  | 0.5 | GCP#4 | 1 |  | Timer 5 sec
32 | TCTO | D/G#1 | EXH. GAS T/C OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#1 | 1 |  | As per "TCTO"
| TCTO | D/G#2 | EXH. GAS T/C OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#2 | 1 |  | As per "TCTO"
| TCTO | D/G#3 | EXH. GAS T/C OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#3 | 1 |  | As per "TCTO"
| TCTO | D/G#4 | EXH. GAS T/C OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#4 | 1 |  | As per "TCTO"
33 | 69WC | D/G#1 | Cooler water flow relay | ON BELOW 40m³/h | Digital |  |  |  | 0.5 | GCP#1 | 1 |  | Timer 10 sec
| 69WC | D/G#2 | Cooler water flow relay | ON BELOW 40m³/h | Digital |  |  |  | 0.5 | GCP#2 | 1 |  | Timer 10 sec
| 69WC | D/G#3 | Cooler water flow relay | ON BELOW 40m³/h | Digital |  |  |  | 0.5 | GCP#3 | 1 |  | Timer 10 sec
| 69WC | D/G#4 | Cooler water flow relay | ON BELOW 40m³/h | Digital |  |  |  | 0.5 | GCP#4 | 1 |  | Timer 10 sec
34 | 63AC |  | Air receiver press switch for engine | On: Below 2.16MPa, Off: 2.94MPa | Digital |  |  |  | 0.5 | GCP | 1
| 63AC |  | Air receiver press switch for engine | On: Below 2.16MPa, Off: 2.94MPa | Digital |  |  |  | 0.5 | GCP | 1
| 63AC |  | Air receiver press switch for engine | On: Below 2.16MPa, Off: 2.94MPa | Digital |  |  |  | 0.5 | GCP | 1
35 | 63AL |  | Air receiver press switch for engine | On: Below 1.77MPa | Digital |  |  |  | 0.5 | GCP | 1
| 63AL |  | Air receiver press switch for engine | On: Below 1.77MPa | Digital |  |  |  | 0.5 | GCP | 1
| 63AL |  | Air receiver press switch for engine | On: Below 1.77MPa | Digital |  |  |  | 0.5 | GCP | 1
36 | 33WCH | D/G#1 | Level switch for C.W. expansion tank | On: above ___L, | Digital |  |  |  | 0.5 | GCP#1 | 1
| 33WCH | D/G#2 | Level switch for C.W. expansion tank | On: above ___L, | Digital |  |  |  | 0.5 | GCP#2 | 1
| 33WCH | D/G#3 | Level switch for C.W. expansion tank | On: above ___L, | Digital |  |  |  | 0.5 | GCP#3 | 1
| 33WCH | D/G#4 | Level switch for C.W. expansion tank | On: above ___L, | Digital |  |  |  | 0.5 | GCP#4 | 1
37 | 33WCL | D/G#1 | Level switch for C.W. expansion tank | On: below ___L, | Digital |  |  |  | 0.5 | GCP#1 | 1
| 33WCL | D/G#2 | Level switch for C.W. expansion tank | On: below ___L, | Digital |  |  |  | 0.5 | GCP#2 | 1
| 33WCL | D/G#3 | Level switch for C.W. expansion tank | On: below ___L, | Digital |  |  |  | 0.5 | GCP#3 | 1
| 33WCL | D/G#4 | Level switch for C.W. expansion tank | On: below ___L, | Digital |  |  |  | 0.5 | GCP#4 | 1
38 | 33WJH | D/G#1 | Level switch for J.W. expansion tank | On: above ___L, | Digital |  |  |  | 0.5 | GCP#1 | 1 |  | Sensor by Ormin, timer 5 sec
| 33WJH | D/G#2 | Level switch for J.W. expansion tank | On: above ___L, | Digital |  |  |  | 0.5 | GCP#2 | 1 |  | Sensor by Ormin, timer 5 sec
| 33WJH | D/G#3 | Level switch for J.W. expansion tank | On: above ___L, | Digital |  |  |  | 0.5 | GCP#3 | 1 |  | Sensor by Ormin, timer 5 sec
| 33WJH | D/G#4 | Level switch for J.W. expansion tank | On: above ___L, | Digital |  |  |  | 0.5 | GCP#4 | 1 |  | Sensor by Ormin, timer 5 sec
39 | 33WJL | D/G#1 | Level switch for J.W. expansion tank | On: below ___L, | Digital |  |  |  | 0.5 | GCP#1 | 1 |  | Sensor by Ormin, timer 5 sec
| 33WJL | D/G#2 | Level switch for J.W. expansion tank | On: below ___L, | Digital |  |  |  | 0.5 | GCP#2 | 1 |  | Sensor by Ormin, timer 5 sec
| 33WJL | D/G#3 | Level switch for J.W. expansion tank | On: below ___L, | Digital |  |  |  | 0.5 | GCP#3 | 1 |  | Sensor by Ormin, timer 5 sec
| 33WJL | D/G#4 | Level switch for J.W. expansion tank | On: below ___L, | Digital |  |  |  | 0.5 | GCP#4 | 1 |  | Sensor by Ormin, timer 5 sec
40 | 33FDH | D/G#1 | Level switch for DO service tank level high | On: above ___L, | Digital |  |  |  | 0.5 | GCP#1 | 1 |  | timer 5 sec
| 33FDH | D/G#2 | Level switch for DO service tank level high | On: above ___L, | Digital |  |  |  | 0.5 | GCP#2 | 1 |  | timer 5 sec
| 33FDH | D/G#3 | Level switch for DO service tank level high | On: above ___L, | Digital |  |  |  | 0.5 | GCP#3 | 1 |  | timer 5 sec
| 33FDH | D/G#4 | Level switch for DO service tank level high | On: above ___L, | Digital |  |  |  | 0.5 | GCP#4 | 1 |  | timer 5 sec
41 | 33FDL | D/G#1 | Level switch for DO service tank level low | On: below ___L, | Digital |  |  |  | 0.5 | GCP#1 | 1 |  | timer 5 sec
| 33FDL | D/G#2 | Level switch for DO service tank level low | On: below ___L, | Digital |  |  |  | 0.5 | GCP#2 | 1 |  | timer 5 sec
| 33FDL | D/G#3 | Level switch for DO service tank level low | On: below ___L, | Digital |  |  |  | 0.5 | GCP#3 | 1 |  | timer 5 sec
| 33FDL | D/G#4 | Level switch for DO service tank level low | On: below ___L, | Digital |  |  |  | 0.5 | GCP#4 | 1 |  | timer 5 sec
42 | 33FDC | D/G#1 | Level switch for DO service tank level control | On: below ___L, Off: above ____L | Digital |  |  |  | 0.5 | GCP#1 | 1 |  | timer 5 sec
| 33FDC | D/G#2 | Level switch for DO service tank level low | On: below ___L, Off: above ____L | Digital |  |  |  | 0.5 | GCP#2 | 1 |  | timer 5 sec
| 33FDC | D/G#3 | Level switch for DO service tank level low | On: below ___L, Off: above ____L | Digital |  |  |  | 0.5 | GCP#3 | 1 |  | timer 5 sec
| 33FDC | D/G#4 | Level switch for DO service tank level low | On: below ___L, Off: above ____L | Digital |  |  |  | 0.5 | GCP#4 | 1 |  | timer 5 sec
43 | 33SETH | D/G#1 | Level switch for HO settling tank level high | On: above ___L, | Digital |  |  |  | 0.5 | GCP#1 | 1 |  | timer 5 sec
| 33SETH | D/G#2 | Level switch for HO settling tank level high | On: above ___L, | Digital |  |  |  | 0.5 | GCP#2 | 1 |  | timer 5 sec
| 33SETH | D/G#3 | Level switch for HO settling tank level high | On: above ___L, | Digital |  |  |  | 0.5 | GCP#3 | 1 |  | timer 5 sec
| 33SETH | D/G#4 | Level switch for HO settling tank level high | On: above ___L, | Digital |  |  |  | 0.5 | GCP#4 | 1 |  | timer 5 sec
44 | 33SETL | D/G#1 | Level switch for HO settling tank level low | On: below ___L, | Digital |  |  |  | 0.5 | GCP#1 | 1 |  | timer 5 sec
| 33SETL | D/G#2 | Level switch for HO settling tank level low | On: below ___L, | Digital |  |  |  | 0.5 | GCP#2 | 1 |  | timer 5 sec
| 33SETL | D/G#3 | Level switch for HO settling tank level low | On: below ___L, | Digital |  |  |  | 0.5 | GCP#3 | 1 |  | timer 5 sec
| 33SETL | D/G#4 | Level switch for HO settling tank level low | On: below ___L, | Digital |  |  |  | 0.5 | GCP#4 | 1 |  | timer 5 sec
45 | 33SETC | D/G#1 | Level switch for HO settling tank level control | On: below ___L, Off: above ____L | Digital |  |  |  | 0.5 | GCP#1 | 1 |  | timer 5 sec
| 33SETC | D/G#2 | Level switch for HO settling tank level low | On: below ___L, Off: above ____L | Digital |  |  |  | 0.5 | GCP#2 | 1 |  | timer 5 sec
| 33SETC | D/G#3 | Level switch for HO settling tank level low | On: below ___L, Off: above ____L | Digital |  |  |  | 0.5 | GCP#3 | 1 |  | timer 5 sec
| 33SETC | D/G#4 | Level switch for HO settling tank level low | On: below ___L, Off: above ____L | Digital |  |  |  | 0.5 | GCP#4 | 1 |  | timer 5 sec
46 | 33SEL | D/G#1 | Level switch for HO service tank level low | On: below ___L, | Digital |  |  |  | 0.5 | GCP#1 | 1 |  | timer 5 sec
| 33SEL | D/G#2 | Level switch for HO service tank level low | On: below ___L, | Digital |  |  |  | 0.5 | GCP#2 | 1 |  | timer 5 sec
| 33SEL | D/G#3 | Level switch for HO service tank level low | On: below ___L, | Digital |  |  |  | 0.5 | GCP#3 | 1 |  | timer 5 sec
| 33SEL | D/G#4 | Level switch for HO service tank level low | On: below ___L, | Digital |  |  |  | 0.5 | GCP#4 | 1 |  | timer 5 sec
47 | 63F | D/G#1 | F.O press.switch | ON BELOW 0.15MPa | Digital |  |  |  | 0.5 | GCP#1 | 1 |  | As per "PTFO"
| 63F | D/G#2 | F.O press.switch | ON BELOW 0.15MPa | Digital |  |  |  | 0.5 | GCP#2 | 1 |  | As per "PTFO"
| 63F | D/G#3 | F.O press.switch | ON BELOW 0.15MPa | Digital |  |  |  | 0.5 | GCP#3 | 1 |  | As per "PTFO"
| 63F | D/G#4 | F.O press.switch | ON BELOW 0.15MPa | Digital |  |  |  | 0.5 | GCP#4 | 1 |  | As per "PTFO"
48 | 33FDRC | D/G#1 | Level switch for F.O drain tank level control | On: below ___L, Off: above ____L | Digital |  |  |  | 0.5 | GCP#1 | 1
| 33FDRC | D/G#2 | Level switch for F.O drain tank | On: below ___L, Off: above ____L | Digital |  |  |  | 0.5 | GCP#2 | 1
| 33FDRC | D/G#3 | Level switch for F.O drain tank | On: below ___L, Off: above ____L | Digital |  |  |  | 0.5 | GCP#3 | 1
| 33FDRC | D/G#4 | Level switch for F.O drain tank | On: below ___L, Off: above ____L | Digital |  |  |  | 0.5 | GCP#4 | 1
49 | 33FDRH | D/G#1 | Level switch for F.O drain tank | On: above ___L, | Digital |  |  |  | 0.5 | GCP#1 | 1
| 33FDRH | D/G#2 | Level switch for F.O drain tank | On: above ___L, | Digital |  |  |  | 0.5 | GCP#2 | 1
| 33FDRH | D/G#3 | Level switch for F.O drain tank | On: above ___L, | Digital |  |  |  | 0.5 | GCP#3 | 1
| 33FDRH | D/G#4 | Level switch for F.O drain tank | On: above ___L, | Digital |  |  |  | 0.5 | GCP#4 | 1
50 | 63FB | D/G#1 | Press switch for auto back wash filter | ON OVER 0.06MPa | Digital |  |  |  | 0.5 | D/G#1 | 1
| 63FB | D/G#2 | Press switch for auto back wash filter | ON OVER 0.06MPa | Digital |  |  |  | 0.5 | D/G#2 | 1
| 63FB | D/G#3 | Press switch for auto back wash filter | ON OVER 0.06MPa | Digital |  |  |  | 0.5 | D/G#3 | 1
| 63FB | D/G#4 | Press switch for auto back wash filter | ON OVER 0.06MPa | Digital |  |  |  | 0.5 | D/G#4 | 1
51 |  | D/G#1 | Display failure |  | Digital |  |  |  | 0.5 | GCP#1 | 1
|  | D/G#2 | Display failure |  | Digital |  |  |  | 0.5 | GCP#2 | 1
|  | D/G#3 | Display failure |  | Digital |  |  |  | 0.5 | GCP#3 | 1
|  | D/G#4 | Display failure |  | Digital |  |  |  | 0.5 | GCP#4 | 1
52 |  | D/G#1 | DC100V source abnormal |  | Digital |  |  |  | 0.5 | GCP#1 | 1
|  | D/G#2 | DC100V source abnormal |  | Digital |  |  |  | 0.5 | GCP#2 | 1
|  | D/G#3 | DC100V source abnormal |  | Digital |  |  |  | 0.5 | GCP#3 | 1
|  | D/G#4 | DC100V source abnormal |  | Digital |  |  |  | 0.5 | GCP#4 | 1
53 |  | D/G#1 | DC24V source abnormal |  | Digital |  |  |  | 0.5 | GCP#1 | 1
|  | D/G#2 | DC24V source abnormal |  | Digital |  |  |  | 0.5 | GCP#2 | 1
|  | D/G#3 | DC24V source abnormal |  | Digital |  |  |  | 0.5 | GCP#3 | 1
|  | D/G#4 | DC24V source abnormal |  | Digital |  |  |  | 0.5 | GCP#4 | 1
54 |  | D/G#1 | Auto synchro failure |  | Digital |  |  |  | 0.5 | GCP#1 | 1
|  | D/G#2 | Auto synchro failure |  | Digital |  |  |  | 0.5 | GCP#2 | 1
|  | D/G#3 | Auto synchro failure |  | Digital |  |  |  | 0.5 | GCP#3 | 1
|  | D/G#4 | Auto synchro failure |  | Digital |  |  |  | 0.5 | GCP#4 | 1
55 |  | D/G#1 | CB non-close |  | Digital |  |  |  | 0.5 | GCP#1 | 1
|  | D/G#2 | CB non-close |  | Digital |  |  |  | 0.5 | GCP#2 | 1
|  | D/G#3 | CB non-close |  | Digital |  |  |  | 0.5 | GCP#3 | 1
|  | D/G#4 | CB non-close |  | Digital |  |  |  | 0.5 | GCP#4 | 1
56 | 63AS |  | Control air press.switch | ON BELOW 0.60MPa | Digital |  |  |  | 0.5 | GCP | 1 |  | Timer 10 sec
| 63AS |  | Control air press.switch | ON BELOW 0.60MPa | Digital |  |  |  | 0.5 | GCP | 1 |  | Timer 10 sec
| 63AS |  | Control air press.switch | ON BELOW 0.60MPa | Digital |  |  |  | 0.5 | GCP | 1 |  | Timer 10 sec
| 63AS |  | Control air press.switch | ON BELOW 0.60MPa | Digital |  |  |  | 0.5 | GCP | 1 |  | Timer 10 sec
60 | 12M | D/G#1 | Over Speed (mechanical side) | ON OVER 113% (+0%, -3%) [813.6min-1(113%)] | Digital |  |  |  | 0.5 | D/G#1 | 1
| 12M | D/G#2 | Over Speed (mechanical side) | ON OVER 113% (+0%, -3%) [813.6min-1(113%)] | Digital |  |  |  | 0.5 | D/G#2 | 1
| 12M | D/G#3 | Over Speed (mechanical side) | ON OVER 113% (+0%, -3%) [813.6min-1(113%)] | Digital |  |  |  | 0.5 | D/G#3 | 1
| 12M | D/G#4 | Over Speed (mechanical side) | ON OVER 113% (+0%, -3%) [813.6min-1(113%)] | Digital |  |  |  | 0.5 | D/G#4 | 1
61 | 26G1 | D/G#1 | Thermal switch for alternator beaing(Fly-wheel side) | ON OVER THE UPPER LIMIT | Digital |  |  |  | 0.5 | GCP#1 | 1
| 26G1 | D/G#2 | Thermal switch for alternator beaing(Fly-wheel side) | ON OVER THE UPPER LIMIT | Digital |  |  |  | 0.5 | GCP#2 | 1
| 26G1 | D/G#3 | Thermal switch for alternator beaing(Fly-wheel side) | ON OVER THE UPPER LIMIT | Digital |  |  |  | 0.5 | GCP#3 | 1
| 26G1 | D/G#4 | Thermal switch for alternator beaing(Fly-wheel side) | ON OVER THE UPPER LIMIT | Digital |  |  |  | 0.5 | GCP#4 | 1
62 | 26G2 | D/G#1 | Thermal switch for alternator beaing (Anti-Fly-wheel side) | ON OVER THE UPPER LIMIT | Digital |  |  |  | 0.5 | GCP#1 | 1
| 26G2 | D/G#2 | Thermal switch for alternator beaing (Anti-Fly-wheel side) | ON OVER THE UPPER LIMIT | Digital |  |  |  | 0.5 | GCP#2 | 1
| 26G2 | D/G#3 | Thermal switch for alternator beaing (Anti-Fly-wheel side) | ON OVER THE UPPER LIMIT | Digital |  |  |  | 0.5 | GCP#3 | 1
| 26G2 | D/G#4 | Thermal switch for alternator beaing (Anti-Fly-wheel side) | ON OVER THE UPPER LIMIT | Digital |  |  |  | 0.5 | GCP#4 | 1
65 | 13 | D/G#1 | RATED SPEED | ON OVER 90% [648min-1(90%)] | Digital |  |  |  | 0.5 | GCP#1 | 1
| 13 | D/G#2 | RATED SPEED | ON OVER 90% [648min-1(90%)] | Digital |  |  |  | 0.5 | GCP#2 | 1
| 13 | D/G#3 | RATED SPEED | ON OVER 90% [648min-1(90%)] | Digital |  |  |  | 0.5 | GCP#3 | 1
| 13 | D/G#4 | RATED SPEED | ON OVER 90% [648min-1(90%)] | Digital |  |  |  | 0.5 | GCP#4 | 1
66 | 14 | D/G#1 | LOW SPEED | ON OVER 300min-1[300min-1(41.67%)] | Digital |  |  |  | 0.5 | GCP#1 | 1
| 14 | D/G#2 | LOW SPEED | ON OVER 300min-1[300min-1(41.67%)] | Digital |  |  |  | 0.5 | GCP#2 | 1
| 14 | D/G#3 | LOW SPEED | ON OVER 300min-1[300min-1(41.67%)] | Digital |  |  |  | 0.5 | GCP#3 | 1
| 14 | D/G#4 | LOW SPEED | ON OVER 300min-1[300min-1(41.67%)] | Digital |  |  |  | 0.5 | GCP#4 | 1
67 | 88V | D/G#1 | STARTING SOLENOID VALVE | WHEN START ENGINE, VALVE OPEN BY EXCITING DC24V, 15W | Digital |  |  |  | 0.5 | GCP#1 | 1
| 88V | D/G#2 | STARTING SOLENOID VALVE | WHEN START ENGINE, VALVE OPEN BY EXCITING DC24V, 15W | Digital |  |  |  | 0.5 | GCP#2 | 1
| 88V | D/G#3 | STARTING SOLENOID VALVE | WHEN START ENGINE, VALVE OPEN BY EXCITING DC24V, 15W | Digital |  |  |  | 0.5 | GCP#3 | 1
| 88V | D/G#4 | STARTING SOLENOID VALVE | WHEN START ENGINE, VALVE OPEN BY EXCITING DC24V, 15W | Digital |  |  |  | 0.5 | GCP#4 | 1
68 | 5V | D/G#1 | FUEL SHUT DOWN DEVICE | WHEN STOP ENGINE, VALVE SHUT BY EXCITING DC24V, 15W | Digital |  |  |  | 0.5 | GCP#1 | 1
| 5V | D/G#2 | FUEL SHUT DOWN DEVICE | WHEN STOP ENGINE, VALVE SHUT BY EXCITING DC24V, 15W | Digital |  |  |  | 0.5 | GCP#2 | 1
| 5V | D/G#3 | FUEL SHUT DOWN DEVICE | WHEN STOP ENGINE, VALVE SHUT BY EXCITING DC24V, 15W | Digital |  |  |  | 0.5 | GCP#3 | 1
| 5V | D/G#4 | FUEL SHUT DOWN DEVICE | WHEN STOP ENGINE, VALVE SHUT BY EXCITING DC24V, 15W | Digital |  |  |  | 0.5 | GCP#4 | 1
69 | 88L | D/G#1 | FUEL CONTROL PISTON MAGNETIC VALVE | WHEN START ENGINE, VALVE OPEN BY EXCITING DC24V, 15W | Digital |  |  |  | 0.5 | GCP#1 | 1
| 88L | D/G#2 | FUEL CONTROL PISTON MAGNETIC VALVE | WHEN START ENGINE, VALVE OPEN BY EXCITING DC24V, 15W | Digital |  |  |  | 0.5 | GCP#2 | 1
| 88L | D/G#3 | FUEL CONTROL PISTON MAGNETIC VALVE | WHEN START ENGINE, VALVE OPEN BY EXCITING DC24V, 15W | Digital |  |  |  | 0.5 | GCP#3 | 1
| 88L | D/G#4 | FUEL CONTROL PISTON MAGNETIC VALVE | WHEN START ENGINE, VALVE OPEN BY EXCITING DC24V, 15W | Digital |  |  |  | 0.5 | GCP#4 | 1
70 | 5S | D/G#1 | FUEL OIL CUT PISTON MAGNETIC VALVE | WHEN STOP ENGINE, VALVE SHUT BY EXCITING DC24V, 15W | Digital |  |  |  | 0.5 | GCP#1 | 1
| 5S | D/G#2 | FUEL OIL CUT PISTON MAGNETIC VALVE | WHEN STOP ENGINE, VALVE SHUT BY EXCITING DC24V, 15W | Digital |  |  |  | 0.5 | GCP#2 | 1
| 5S | D/G#3 | FUEL OIL CUT PISTON MAGNETIC VALVE | WHEN STOP ENGINE, VALVE SHUT BY EXCITING DC24V, 15W | Digital |  |  |  | 0.5 | GCP#3 | 1
| 5S | D/G#4 | FUEL OIL CUT PISTON MAGNETIC VALVE | WHEN STOP ENGINE, VALVE SHUT BY EXCITING DC24V, 15W | Digital |  |  |  | 0.5 | GCP#4 | 1
71 | MDMO | D/G#1 | MONITORING OF OIL MIST LEVEL | 0-2.0mg/L_4-20mA | Analog |  |  |  | 0.5 | GCP#1 | 1
| MDMO | D/G#2 | MONITORING OF OIL MIST LEVEL | 0-2.0mg/L_4-20mA | Analog |  |  |  | 0.5 | GCP#2 | 1
| MDMO | D/G#3 | MONITORING OF OIL MIST LEVEL | 0-2.0mg/L_4-20mA | Analog |  |  |  | 0.5 | GCP#3 | 1
| MDMO | D/G#4 | MONITORING OF OIL MIST LEVEL | 0-2.0mg/L_4-20mA | Analog |  |  |  | 0.5 | GCP#4 | 1
72 | HS | D/G#1 | GOVERNOR HANDLE SWITCH | ON: ENGINE START CONDITION | Digital |  |  |  | 0.5 | GCP#1 | 1
| HS | D/G#2 | GOVERNOR HANDLE SWITCH | ON: ENGINE START CONDITION | Digital |  |  |  | 0.5 | GCP#2 | 1
| HS | D/G#3 | GOVERNOR HANDLE SWITCH | ON: ENGINE START CONDITION | Digital |  |  |  | 0.5 | GCP#3 | 1
| HS | D/G#4 | GOVERNOR HANDLE SWITCH | ON: ENGINE START CONDITION | Digital |  |  |  | 0.5 | GCP#4 | 1
73 | 33T | D/G#1 | TURNING HANDLE POSITION SWITCH(ON AT TURNING DEVICE OUT) | ON: ENGINE START CONDITION | Digital |  |  |  | 0.5 | GCP#1 | 1
| 33T | D/G#2 | TURNING HANDLE POSITION SWITCH(ON AT TURNING DEVICE OUT) | ON: ENGINE START CONDITION | Digital |  |  |  | 0.5 | GCP#2 | 1
| 33T | D/G#3 | TURNING HANDLE POSITION SWITCH(ON AT TURNING DEVICE OUT) | ON: ENGINE START CONDITION | Digital |  |  |  | 0.5 | GCP#3 | 1
| 33T | D/G#4 | TURNING HANDLE POSITION SWITCH(ON AT TURNING DEVICE OUT) | ON: ENGINE START CONDITION | Digital |  |  |  | 0.5 | GCP#4 | 1
74 | 1B(U) | D/G#1 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  |  |  | 0.5 | GCP#1 | 1
| 1B(U) | D/G#2 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  |  |  | 0.5 | GCP#2 | 1
| 1B(U) | D/G#3 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  |  |  | 0.5 | GCP#3 | 1
| 1B(U) | D/G#4 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  |  |  | 0.5 | GCP#4 | 1
75 | 2B(V) | D/G#1 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  |  |  | 0.5 | GCP#1 | 1
| 2B(V) | D/G#2 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  |  |  | 0.5 | GCP#2 | 1
| 2B(V) | D/G#3 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  |  |  | 0.5 | GCP#3 | 1
| 2B(V) | D/G#4 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  |  |  | 0.5 | GCP#4 | 1
76 | 3B(W) | D/G#1 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  |  |  | 0.5 | GCP#1 | 1
| 3B(W) | D/G#2 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  |  |  | 0.5 | GCP#2 | 1
| 3B(W) | D/G#3 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  |  |  | 0.5 | GCP#3 | 1
| 3B(W) | D/G#4 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  |  |  | 0.5 | GCP#4 | 1
77 | 4B(U) | D/G#1 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#1 | 1
| 4B(U) | D/G#2 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#2 | 1
| 4B(U) | D/G#3 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#3 | 1
| 4B(U) | D/G#4 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#4 | 1
78 | 5B(V) | D/G#1 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#1 | 1
| 5B(V) | D/G#2 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#2 | 1
| 5B(V) | D/G#3 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#3 | 1
| 5B(V) | D/G#4 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#4 | 1
79 | 6B(W) | D/G#1 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#1 | 1
| 6B(W) | D/G#2 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#2 | 1
| 6B(W) | D/G#3 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#3 | 1
| 6B(W) | D/G#4 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#4 | 1
80 | 38G1 | D/G#1 | GENERATOR BEARING THERMAL SENSOR (FLY-WHEEL SIDE) | PT 100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#1 | 1
| 38G1 | D/G#2 | GENERATOR BEARING THERMAL SENSOR (FLY-WHEEL SIDE) | PT 100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#2 | 1
| 38G1 | D/G#3 | GENERATOR BEARING THERMAL SENSOR (FLY-WHEEL SIDE) | PT 100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#3 | 1
| 38G1 | D/G#4 | GENERATOR BEARING THERMAL SENSOR (FLY-WHEEL SIDE) | PT 100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#4 | 1
81 | 38G2 | D/G#1 | GENERATOR BEARING THERMAL SENSOR (ANTI-FLY-WHEEL SIDE) | PT 100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#1 | 1
| 38G2 | D/G#2 | GENERATOR BEARING THERMAL SENSOR (ANTI-FLY-WHEEL SIDE) | PT 100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#2 | 1
| 38G2 | D/G#3 | GENERATOR BEARING THERMAL SENSOR (ANTI-FLY-WHEEL SIDE) | PT 100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#3 | 1
| 38G2 | D/G#4 | GENERATOR BEARING THERMAL SENSOR (ANTI-FLY-WHEEL SIDE) | PT 100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#4 | 1
82 | TC1 | D/G#1 | EXH. GAS No. 1 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#1 | 1
| TC1 | D/G#2 | EXH. GAS No. 1 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#2 | 1
| TC1 | D/G#3 | EXH. GAS No. 1 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#3 | 1
| TC1 | D/G#4 | EXH. GAS No. 1 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#4 | 1
83 | TC2 | D/G#1 | EXH. GAS No. 2 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#1 | 1
| TC2 | D/G#2 | EXH. GAS No. 2 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#2 | 1
| TC2 | D/G#3 | EXH. GAS No. 2 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#3 | 1
| TC2 | D/G#4 | EXH. GAS No. 2 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#4 | 1
84 | TC3 | D/G#1 | EXH. GAS No. 3 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#1 | 1
| TC3 | D/G#2 | EXH. GAS No. 3 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#2 | 1
| TC3 | D/G#3 | EXH. GAS No. 3 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#3 | 1
| TC3 | D/G#4 | EXH. GAS No. 3 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#4 | 1
85 | TC4 | D/G#1 | EXH. GAS No. 4 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#1 | 1
| TC4 | D/G#2 | EXH. GAS No. 4 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#2 | 1
| TC4 | D/G#3 | EXH. GAS No. 4 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#3 | 1
| TC4 | D/G#4 | EXH. GAS No. 4 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#4 | 1
86 | TC5 | D/G#1 | EXH. GAS No. 5 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#1 | 1
| TC5 | D/G#2 | EXH. GAS No. 5 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#2 | 1
| TC5 | D/G#3 | EXH. GAS No. 5 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#3 | 1
| TC5 | D/G#4 | EXH. GAS No. 5 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#4 | 1
87 | TC6 | D/G#1 | EXH. GAS No. 6 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#1 | 1
| TC6 | D/G#2 | EXH. GAS No. 6 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#2 | 1
| TC6 | D/G#3 | EXH. GAS No. 6 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#3 | 1
| TC6 | D/G#4 | EXH. GAS No. 6 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#4 | 1
88 | TCTI | D/G#1 | EXH. GAS T/C IN | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#1 | 1
| TCTI | D/G#2 | EXH. GAS T/C IN | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#2 | 1
| TCTI | D/G#3 | EXH. GAS T/C IN | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#3 | 1
| TCTI | D/G#4 | EXH. GAS T/C IN | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  |  |  | 0.5 | GCP#4 | 1
89 | FOT | D/G#1 | D.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SERVICE TANK) | 1 Litre/1 pulse | Analog |  |  |  | 0.5 | GCP#1 | 1
| FOT | D/G#2 | D.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SERVICE TANK) | 1 Litre/1 pulse | Analog |  |  |  | 0.5 | GCP#2 | 1
| FOT | D/G#3 | D.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SERVICE TANK) | 1 Litre/1 pulse | Analog |  |  |  | 0.5 | GCP#3 | 1
| FOT | D/G#4 | D.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SERVICE TANK) | 1 Litre/1 pulse | Analog |  |  |  | 0.5 | GCP#4 | 1
90 | FOEI | D/G#1 | D.O. FLOW METER FOR ENGINE INLET | 1 Litre/1 pulse | Analog |  |  |  | 0.5 | GCP#1 | 1
| FOEI | D/G#2 | D.O. FLOW METER FOR ENGINE INLET | 1 Litre/1 pulse | Analog |  |  |  | 0.5 | GCP#2 | 1
| FOEI | D/G#3 | D.O. FLOW METER FOR ENGINE INLET | 1 Litre/1 pulse | Analog |  |  |  | 0.5 | GCP#3 | 1
| FOEI | D/G#4 | D.O. FLOW METER FOR ENGINE INLET | 1 Litre/1 pulse | Analog |  |  |  | 0.5 | GCP#4 | 1
91 | FOEO | D/G#1 | D.O. FLOW METER FOR ENGINE OUTLET | 1 Litre/1 pulse | Analog |  |  |  | 0.5 | GCP#1 | 1
| FOEO | D/G#2 | D.O. FLOW METER FOR ENGINE OUTLET | 1 Litre/1 pulse | Analog |  |  |  | 0.5 | GCP#2 | 1
| FOEO | D/G#3 | D.O. FLOW METER FOR ENGINE OUTLET | 1 Litre/1 pulse | Analog |  |  |  | 0.5 | GCP#3 | 1
| FOEO | D/G#4 | D.O. FLOW METER FOR ENGINE OUTLET | 1 Litre/1 pulse | Analog |  |  |  | 0.5 | GCP#4 | 1
92 | FOHT | D/G#1 | H.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SETTLING TANK) | 1 Litre/1 pulse | Analog |  |  |  | 0.5 | GCP#1 | 1
| FOHT | D/G#2 | H.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SETTLING TANK) | 1 Litre/1 pulse | Analog |  |  |  | 0.5 | GCP#2 | 1
| FOHT | D/G#3 | H.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SETTLING TANK) | 1 Litre/1 pulse | Analog |  |  |  | 0.5 | GCP#3 | 1
| FOHT | D/G#4 | H.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SETTLING TANK) | 1 Litre/1 pulse | Analog |  |  |  | 0.5 | GCP#4 | 1
93 | FOHEI | D/G#1 | H.O. FLOW METER FOR ENGINE INLET | 1 Litre/1 pulse | Analog |  |  |  | 0.5 | GCP#1 | 1
| FOHEI | D/G#2 | H.O. FLOW METER FOR ENGINE INLET | 1 Litre/1 pulse | Analog |  |  |  | 0.5 | GCP#2 | 1
| FOHEI | D/G#3 | H.O. FLOW METER FOR ENGINE INLET | 1 Litre/1 pulse | Analog |  |  |  | 0.5 | GCP#3 | 1
| FOHEI | D/G#4 | H.O. FLOW METER FOR ENGINE INLET | 1 Litre/1 pulse | Analog |  |  |  | 0.5 | GCP#4 | 1
94 | FOHEO | D/G#1 | H.O. FLOW METER FOR ENGINE OUTLET | 1 Litre/1 pulse | Analog |  |  |  | 0.5 | GCP#1 | 1
| FOHEO | D/G#2 | H.O. FLOW METER FOR ENGINE OUTLET | 1 Litre/1 pulse | Analog |  |  |  | 0.5 | GCP#2 | 1
| FOHEO | D/G#3 | H.O. FLOW METER FOR ENGINE OUTLET | 1 Litre/1 pulse | Analog |  |  |  | 0.5 | GCP#3 | 1
| FOHEO | D/G#4 | H.O. FLOW METER FOR ENGINE OUTLET | 1 Litre/1 pulse | Analog |  |  |  | 0.5 | GCP#4 | 1
95 | PTFO | D/G#1 | PRESS. SENSOR FOR FUEL OIL | 0-1.0MPa / 4-20mA | Analog |  |  |  | 0.5 | GCP#1 | 1
| PTFO | D/G#2 | PRESS. SENSOR FOR FUEL OIL | 0-1.0MPa / 4-20mA | Analog |  |  |  | 0.5 | GCP#2 | 1
| PTFO | D/G#3 | PRESS. SENSOR FOR FUEL OIL | 0-1.0MPa / 4-20mA | Analog |  |  |  | 0.5 | GCP#3 | 1
| PTFO | D/G#4 | PRESS. SENSOR FOR FUEL OIL | 0-1.0MPa / 4-20mA | Analog |  |  |  | 0.5 | GCP#4 | 1
96 | PTJW | D/G#1 | PRESS. SENSOR FOR JACKET WATER | 0-0.6MPa / 4-20mA | Analog |  |  |  | 0.5 | GCP#1 | 1
| PTJW | D/G#2 | PRESS. SENSOR FOR JACKET WATER | 0-0.6MPa / 4-20mA | Analog |  |  |  | 0.5 | GCP#2 | 1
| PTJW | D/G#3 | PRESS. SENSOR FOR JACKET WATER | 0-0.6MPa / 4-20mA | Analog |  |  |  | 0.5 | GCP#3 | 1
| PTJW | D/G#4 | PRESS. SENSOR FOR JACKET WATER | 0-0.6MPa / 4-20mA | Analog |  |  |  | 0.5 | GCP#4 | 1
97 | PTCW | D/G#1 | PRESS. SENSOR FOR COOLER WATER | 0-0.6MPa / 4-20mA | Analog |  |  |  | 0.5 | GCP#1 | 1
| PTCW | D/G#2 | PRESS. SENSOR FOR COOLER WATER | 0-0.6MPa / 4-20mA | Analog |  |  |  | 0.5 | GCP#2 | 1
| PTCW | D/G#3 | PRESS. SENSOR FOR COOLER WATER | 0-0.6MPa / 4-20mA | Analog |  |  |  | 0.5 | GCP#3 | 1
| PTCW | D/G#4 | PRESS. SENSOR FOR COOLER WATER | 0-0.6MPa / 4-20mA | Analog |  |  |  | 0.5 | GCP#4 | 1
98 | PTLO | D/G#1 | PRESS. SENSOR FOR ENGINE L.O. | 0-1.0MPa / 4-20mA | Analog |  |  |  | 0.5 | GCP#1 | 1
| PTLO | D/G#2 | PRESS. SENSOR FOR ENGINE L.O. | 0-1.0MPa / 4-20mA | Analog |  |  |  | 0.5 | GCP#2 | 1
| PTLO | D/G#3 | PRESS. SENSOR FOR ENGINE L.O. | 0-1.0MPa / 4-20mA | Analog |  |  |  | 0.5 | GCP#3 | 1
| PTLO | D/G#4 | PRESS. SENSOR FOR ENGINE L.O. | 0-1.0MPa / 4-20mA | Analog |  |  |  | 0.5 | GCP#4 | 1
99 | PTTL0 | D/G#1 | PRESS. SENSOR FOR TURBO-CHARGER L.O. | 0-1.0MPa / 4-20mA | Analog |  |  |  | 0.5 | GCP#1 | 1
| PTTL0 | D/G#2 | PRESS. SENSOR FOR TURBO-CHARGER L.O. | 0-1.0MPa / 4-20mA | Analog |  |  |  | 0.5 | GCP#2 | 1
| PTTL0 | D/G#3 | PRESS. SENSOR FOR TURBO-CHARGER L.O. | 0-1.0MPa / 4-20mA | Analog |  |  |  | 0.5 | GCP#3 | 1
| PTTL0 | D/G#4 | PRESS. SENSOR FOR TURBO-CHARGER L.O. | 0-1.0MPa / 4-20mA | Analog |  |  |  | 0.5 | GCP#4 | 1
100 | PTIA | D/G#1 | PRESS. SENSOR FOR INTAKE-AIR | 0-0.4MPa / 4-20mA | Analog |  |  |  | 0.5 | GCP#1 | 1
| PTIA | D/G#2 | PRESS. SENSOR FOR INTAKE-AIR | 0-0.4MPa / 4-20mA | Analog |  |  |  | 0.5 | GCP#2 | 1
| PTIA | D/G#3 | PRESS. SENSOR FOR INTAKE-AIR | 0-0.4MPa / 4-20mA | Analog |  |  |  | 0.5 | GCP#3 | 1
| PTIA | D/G#4 | PRESS. SENSOR FOR INTAKE-AIR | 0-0.4MPa / 4-20mA | Analog |  |  |  | 0.5 | GCP#4 | 1
101 | 26EX1 | D/G#1 | TURBO-CHARGER GAS OUTLET TEMP. SWITCH (1st) | On over 400°C | Digital |  |  |  | 0.5 | GCP#1 | 1 |  | T/C Outlet temperature
| 26EX1 | D/G#2 | TURBO-CHARGER GAS OUTLET TEMP. SWITCH (1st) | On over 400°C | Digital |  |  |  | 0.5 | GCP#2 | 1 |  | T/C Outlet temperature
| 26EX1 | D/G#3 | TURBO-CHARGER GAS OUTLET TEMP. SWITCH (1st) | On over 400°C | Digital |  |  |  | 0.5 | GCP#3 | 1 |  | T/C Outlet temperature
| 26EX1 | D/G#4 | TURBO-CHARGER GAS OUTLET TEMP. SWITCH (1st) | On over 400°C | Digital |  |  |  | 0.5 | GCP#4 | 1 |  | T/C Outlet temperature
102 | TRJWI | D/G#1 | TEMP. SENSOR FOR JACKET WATER INLET | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#1 | 1
| TRJWI | D/G#2 | TEMP. SENSOR FOR JACKET WATER INLET | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#2 | 1
| TRJWI | D/G#3 | TEMP. SENSOR FOR JACKET WATER INLET | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#3 | 1
| TRJWI | D/G#4 | TEMP. SENSOR FOR JACKET WATER INLET | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#4 | 1
103 | TRJWO | D/G#1 | TEMP. SENSOR FOR JACKET WATER OUTLET | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#1 | 1
| TRJWO | D/G#2 | TEMP. SENSOR FOR JACKET WATER OUTLET | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#2 | 1
| TRJWO | D/G#3 | TEMP. SENSOR FOR JACKET WATER OUTLET | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#3 | 1
| TRJWO | D/G#4 | TEMP. SENSOR FOR JACKET WATER OUTLET | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#4 | 1
104 | TRCWI | D/G#1 | TEMP. SENSOR FOR COOLER WATER INLET | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#1 | 1
| TRCWI | D/G#2 | TEMP. SENSOR FOR COOLER WATER INLET | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#2 | 1
| TRCWI | D/G#3 | TEMP. SENSOR FOR COOLER WATER INLET | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#3 | 1
| TRCWI | D/G#4 | TEMP. SENSOR FOR COOLER WATER INLET | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#4 | 1
105 | TRCWO | D/G#1 | TEMP. SENSOR FOR COOLER WATER OUTLET | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#1 | 1
| TRCWO | D/G#2 | TEMP. SENSOR FOR COOLER WATER OUTLET | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#2 | 1
| TRCWO | D/G#3 | TEMP. SENSOR FOR COOLER WATER OUTLET | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#3 | 1
| TRCWO | D/G#4 | TEMP. SENSOR FOR COOLER WATER OUTLET | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#4 | 1
106 | TRLOI | D/G#1 | TEMP. SENSOR FOR L.O. COOLER INLET | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#1 | 1
| TRLOI | D/G#2 | TEMP. SENSOR FOR L.O. COOLER INLET | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#2 | 1
| TRLOI | D/G#3 | TEMP. SENSOR FOR L.O. COOLER INLET | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#3 | 1
| TRLOI | D/G#4 | TEMP. SENSOR FOR L.O. COOLER INLET | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#4 | 1
107 | TRLOO | D/G#1 | TEMP. SENSOR FOR L.O. COOLER OUTLET | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#1 | 1
| TRLOO | D/G#2 | TEMP. SENSOR FOR L.O. COOLER OUTLET | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#2 | 1
| TRLOO | D/G#3 | TEMP. SENSOR FOR L.O. COOLER OUTLET | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#3 | 1
| TRLOO | D/G#4 | TEMP. SENSOR FOR L.O. COOLER OUTLET | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#4 | 1
108 | TRCWB | D/G#1 | TEMP. SENSOR FOR COOLER WATER BEFORE L.O. COOLER | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#1 | 1
| TRCWB | D/G#2 | TEMP. SENSOR FOR COOLER WATER BEFORE L.O. COOLER | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#2 | 1
| TRCWB | D/G#3 | TEMP. SENSOR FOR COOLER WATER BEFORE L.O. COOLER | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#3 | 1
| TRCWB | D/G#4 | TEMP. SENSOR FOR COOLER WATER BEFORE L.O. COOLER | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#4 | 1
109 | 26F1S | D/G#1 | Thermostat switch for line heater | On below 25oC, Off over 30oC | Digital |  |  | ` | 0.5 | GCP#1 | 1
| 26F1S | D/G#2 | Thermostat switch for line heater | On below 25oC, Off over 30oC | Digital |  |  | ` | 0.5 | GCP#2 | 1
| 26F1S | D/G#3 | Thermostat switch for line heater | On below 25oC, Off over 30oC | Digital |  |  | ` | 0.5 | GCP#3 | 1
| 26F1S | D/G#4 | Thermostat switch for line heater | On below 25oC, Off over 30oC | Digital |  |  | ` | 0.5 | GCP#4 | 1
110 | (26F1A) |  | Thermostat switch for line heater | On over 60℃ | Digital |  |  |  |  | GCP | 1
111 | PTSA | D/G#1 | PRESS SENSOR FOR AIR RECEIVER | 0-5.0MPa / 4-20mA | Analog |  |  |  | 0.5 | GCP#1 | 1
| PTSA | D/G#2 | PRESS SENSOR FOR AIR RECEIVER | 0-5.0MPa / 4-20mA | Analog |  |  |  | 0.5 | GCP#2 | 1
| PTSA | D/G#3 | PRESS SENSOR FOR AIR RECEIVER | 0-5.0MPa / 4-20mA | Analog |  |  |  | 0.5 | GCP#3 | 1
| PTSA | D/G#4 | PRESS SENSOR FOR AIR RECEIVER | 0-5.0MPa / 4-20mA | Analog |  |  |  | 0.5 | GCP#4 | 1
112 | 26F2S | D/G#1 | Thermostat sensor for HO Settling tank | On below 60oC, Off over 65oC | Digital |  |  |  | 0.5 | GCP#1 | 1
| 26F2S | D/G#2 | Thermostat sensor for HO Settling tank | On below 60oC, Off over 65oC | Digital |  |  |  | 0.5 | GCP#2 | 1
| 26F2S | D/G#3 | Thermostat sensor for HO Settling tank | On below 60oC, Off over 65oC | Digital |  |  |  | 0.5 | GCP#3 | 1
| 26F2S | D/G#4 | Thermostat sensor for HO Settling tank | On below 60oC, Off over 65oC | Digital |  |  |  | 0.5 | GCP#4 | 1
113 | 26F2A |  | (Thermostat sensor for HO Settling tank heater) | On: above 75oC | Digital |  |  |  |  | GCP | 1 |  | Overheat, heater stop operation
114 | 26F3S |  | Thermostat switch for HO Service tank heater | On below 90oC, Off over 95oC | Digital |  |  |  |  | GCP | 1
115 | 26F4 |  | Thermostat switch for HO Service tank(upper) | On over 90oC, Off below 85oC | Digital |  |  |  |  | GCP | 1
116 | 26F3A |  | (Thermostat switch for HO Service tank heater) | On: above 105oC | Digital |  |  |  |  | GCP | 1 |  | Overheat, heater stop operation
117 | 26F7 |  | Thermostat switch for HO Engine inlet | On below 110oC, Off over 115oC | Digital |  |  |  |  | GCP | 1
118 | 26F8 |  | Thermostat switch for HO Engine inlet | On below 130oC, Off below 125oC | Digital |  |  |  |  | GCP | 1
119 | 63FH |  | Press switch for HO piping | On below 0.5MPa | Digital |  |  |  |  | GCP | 1
120 | 63FD |  | Press switch for DO piping | On below 0.35MPa | Digital |  |  |  |  | GCP | 1
121 | LSDO | D/G#1 | Limit switch for change over valve | On D.O.side | Digital |  |  |  | 0.5 | GCP#1 | 1
| LSDO | D/G#1 | Limit switch for change over valve | On D.O.side | Digital |  |  |  | 0.5 | GCP#1 | 1
| LSDO | D/G#2 | Limit switch for change over valve | On D.O.side | Digital |  |  |  | 0.5 | GCP#2 | 1
| LSDO | D/G#2 | Limit switch for change over valve | On D.O.side | Digital |  |  |  | 0.5 | GCP#2 | 1
| LSDO | D/G#3 | Limit switch for change over valve | On D.O.side | Digital |  |  |  | 0.5 | GCP#3 | 1
| LSDO | D/G#3 | Limit switch for change over valve | On D.O.side | Digital |  |  |  | 0.5 | GCP#3 | 1
| LSDO | D/G#4 | Limit switch for change over valve | On D.O.side | Digital |  |  |  | 0.5 | GCP#4 | 1
| LSDO | D/G#4 | Limit switch for change over valve | On D.O.side | Digital |  |  |  | 0.5 | GCP#4 | 1
122 | LSHO | D/G#1 | Limit switch for change over valve | On H.O.side | Digital |  |  |  | 0.5 | GCP#1 | 1
| LSHO | D/G#1 | Limit switch for change over valve | On H.O.side | Digital |  |  |  | 0.5 | GCP#1 | 1
| LSHO | D/G#2 | Limit switch for change over valve | On H.O.side | Digital |  |  |  | 0.5 | GCP#2 | 1
| LSHO | D/G#2 | Limit switch for change over valve | On H.O.side | Digital |  |  |  | 0.5 | GCP#2 | 1
| LSHO | D/G#3 | Limit switch for change over valve | On H.O.side | Digital |  |  |  | 0.5 | GCP#3 | 1
| LSHO | D/G#3 | Limit switch for change over valve | On H.O.side | Digital |  |  |  | 0.5 | GCP#3 | 1
| LSHO | D/G#4 | Limit switch for change over valve | On H.O.side | Digital |  |  |  | 0.5 | GCP#4 | 1
| LSHO | D/G#4 | Limit switch for change over valve | On H.O.side | Digital |  |  |  | 0.5 | GCP#4 | 1
123 | 26F9S |  | Thermostat switch for Drain Tank | On below 50oC, Off below 55oC | Digital |  |  |  |  | GCP | 1
124 | 26F9A |  | (Thermostat switch for Drain Tank Heater) | On: above 65oC | Digital |  |  |  |  | GCP | 1 |  | Overheat, heater stop operation
125 | TRDI | D/G#1 | TEMP. SENSOR for DO Engine inlet | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#1 | 1
| TRDI | D/G#2 | TEMP. SENSOR for DO Engine inlet | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#2 | 1
| TRDI | D/G#3 | TEMP. SENSOR for DO Engine inlet | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#3 | 1
| TRDI | D/G#4 | TEMP. SENSOR for DO Engine inlet | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#4 | 1
126 | TRDO | D/G#1 | TEMP. SENSOR for DO Engine outlet | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#1 | 1
| TRDO | D/G#2 | TEMP. SENSOR for DO Engine outlet | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#2 | 1
| TRDO | D/G#3 | TEMP. SENSOR for DO Engine outlet | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#3 | 1
| TRDO | D/G#4 | TEMP. SENSOR for DO Engine outlet | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#4 | 1
127 | TRHI | D/G#1 | TEMP. SENSOR for HO Engine inlet | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#1 | 1
| TRHI | D/G#2 | TEMP. SENSOR for HO Engine inlet | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#2 | 1
| TRHI | D/G#3 | TEMP. SENSOR for HO Engine inlet | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#3 | 1
| TRHI | D/G#4 | TEMP. SENSOR for HO Engine inlet | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#4 | 1
128 | TRHO | D/G#1 | TEMP. SENSOR for HO Engine outlet | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#1 | 1
| TRHO | D/G#2 | TEMP. SENSOR for HO Engine outlet | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#2 | 1
| TRHO | D/G#3 | TEMP. SENSOR for HO Engine outlet | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#3 | 1
| TRHO | D/G#4 | TEMP. SENSOR for HO Engine outlet | PT100Ω @ 0°C | Analog |  |  |  | 0.5 | GCP#4 | 1
129 |  |  | Viscosity controller | less than 230 CST | Digital |  |  |  | 0.5 |  | 1
130 | TRRA1 | D/G#1 | TEMP. SENSOR FOR RADIATOR 1 | Fault | Digital |  |  |  | 0.5 | D/G#1 | 1
| TRRA1 | D/G#2 | TEMP. SENSOR FOR RADIATOR 1 | Fault | Digital |  |  |  | 0.5 | D/G#2 | 1
| TRRA1 | D/G#3 | TEMP. SENSOR FOR RADIATOR 1 | Fault | Digital |  |  |  | 0.5 | D/G#3 | 1
| TRRA1 | D/G#4 | TEMP. SENSOR FOR RADIATOR 1 | Fault | Digital |  |  |  | 0.5 | D/G#4 | 1
131 | TRRA2 | D/G#1 | TEMP. SENSOR FOR RADIATOR 2 | Fault | Digital |  |  |  | 0.5 | D/G#1 | 1
| TRRA2 | D/G#2 | TEMP. SENSOR FOR RADIATOR 2 | Fault | Digital |  |  |  | 0.5 | D/G#2 | 1
| TRRA2 | D/G#3 | TEMP. SENSOR FOR RADIATOR 2 | Fault | Digital |  |  |  | 0.5 | D/G#3 | 1
| TRRA2 | D/G#4 | TEMP. SENSOR FOR RADIATOR 2 | Fault | Digital |  |  |  | 0.5 | D/G#4 | 1
132 | TRRA3 | D/G#1 | TEMP. SENSOR FOR RADIATOR 3 | Fault | Digital |  |  |  | 0.5 | D/G#1 | 1
| TRRA3 | D/G#2 | TEMP. SENSOR FOR RADIATOR 3 | Fault | Digital |  |  |  | 0.5 | D/G#2 | 1
| TRRA3 | D/G#3 | TEMP. SENSOR FOR RADIATOR 3 | Fault | Digital |  |  |  | 0.5 | D/G#3 | 1
| TRRA3 | D/G#4 | TEMP. SENSOR FOR RADIATOR 3 | Fault | Digital |  |  |  | 0.5 | D/G#4 | 1
133 | TRRA4 | D/G#1 | TEMP. SENSOR FOR RADIATOR 4 | Fault | Digital |  |  |  | 0.5 | D/G#1 | 1
| TRRA4 | D/G#2 | TEMP. SENSOR FOR RADIATOR 4 | Fault | Digital |  |  |  | 0.5 | D/G#2 | 1
| TRRA4 | D/G#3 | TEMP. SENSOR FOR RADIATOR 4 | Fault | Digital |  |  |  | 0.5 | D/G#3 | 1
| TRRA4 | D/G#4 | TEMP. SENSOR FOR RADIATOR 4 | Fault | Digital |  |  |  | 0.5 | D/G#4 | 1
134 | HOPF |  | H.O. Purifier Abnormal |  | Digital |  |  |  | 0.5 | GCP | 1
135 | LOPF |  | Lub.Oil Purifier Abnormal |  | Digital |  |  |  | 0.5 | GCP | 1
136 | MD-SX | D/G#1 | OMD ANALOG OUTPUT BOARD |  | Analog |  |  |  | 0.5 | D/G#1 | 1
| MD-SX | D/G#2 | OMD ANALOG OUTPUT BOARD |  | Analog |  |  |  | 0.5 | D/G#2 | 1
| MD-SX | D/G#3 | OMD ANALOG OUTPUT BOARD |  | Analog |  |  |  | 0.5 | D/G#3 | 1
| MD-SX | D/G#4 | OMD ANALOG OUTPUT BOARD |  | Analog |  |  |  | 0.5 | D/G#4 | 1
137 | 33SD |  | Level Switch for Sludge Tank |  | Digital |  |  |  |  | GCP | 1
140 |  | D/G#1 | Voltage [Generator] | V | Analog |  |  |  | 0.5 | GCP#1 | 1
|  | D/G#2 | Voltage [Generator] | V | Analog |  |  |  | 0.5 | GCP#2 | 1
|  | D/G#3 | Voltage [Generator] | V | Analog |  |  |  | 0.5 | GCP#3 | 1
|  | D/G#4 | Voltage [Generator] | V | Analog |  |  |  | 0.5 | GCP#4 | 1
141 |  | D/G#1 | Frequency [Generator] | Hz | Analog |  |  |  | 0.5 | GCP#1 | 1
|  | D/G#2 | Frequency [Generator] | Hz | Analog |  |  |  | 0.5 | GCP#2 | 1
|  | D/G#3 | Frequency [Generator] | Hz | Analog |  |  |  | 0.5 | GCP#3 | 1
|  | D/G#4 | Frequency [Generator] | Hz | Analog |  |  |  | 0.5 | GCP#4 | 1
佐々木追記 |  | D/G#1 | Power factor [Generator] |  | Analog |  |  |  | 0.5 | GCP#1 | 1
|  | D/G#2 | Power factor [Generator] |  | Analog |  |  |  | 0.5 | GCP#2 | 1
|  | D/G#3 | Power factor [Generator] |  | Analog |  |  |  | 0.5 | GCP#3 | 1
|  | D/G#4 | Power factor [Generator] |  | Analog |  |  |  | 0.5 | GCP#4 | 1
142 | 52G1 |  | VCB Status [Generator][52G1] | Close | Digital |  |  |  | 0.5 | GCP#1 | 1
|  |  |  | Open | Digital |  |  |  | 0.5 | GCP#1 | 1
|  |  |  | Fault (Non-close)/trip | Digital |  |  |  | 0.5 | GCP#1 | 1
| 52G2 |  | VCB Status [Generator][52G1] | Close | Digital |  |  |  | 0.5 | GCP#2 | 1
|  |  |  | Open | Digital |  |  |  | 0.5 | GCP#2 | 1
|  |  |  | Fault (Non-close)/trip | Digital |  |  |  | 0.5 | GCP#2 | 1
| 52G3 |  | VCB Status [Generator][52G1] | Close | Digital |  |  |  | 0.5 | GCP#3 | 1
|  |  |  | Open | Digital |  |  |  | 0.5 | GCP#3 | 1
|  |  |  | Fault (Non-close)/trip | Digital |  |  |  | 0.5 | GCP#3 | 1
| 52G4 |  | VCB Status [Generator][52G1] | Close | Digital |  |  |  | 0.5 | GCP#4 | 1
|  |  |  | Open | Digital |  |  |  | 0.5 | GCP#4 | 1
|  |  |  | Fault (Non-close)/trip | Digital |  |  |  | 0.5 | GCP#4 | 1
143 |  | D/G#1 | Current [Generator] | Amphere | Analog |  |  |  | 0.5 | GCP#1 | 1
|  | D/G#2 | Current [Generator] | Amphere | Analog |  |  |  | 0.5 | GCP#2 | 1
|  | D/G#3 | Current [Generator] | Amphere | Analog |  |  |  | 0.5 | GCP#3 | 1
|  | D/G#4 | Current [Generator] | Amphere | Analog |  |  |  | 0.5 | GCP#4 | 1
144 |  | D/G#1 | Running hours [Generator] | hrs | Analog |  |  |  | 0.5 | GCP#1 | 1
|  | D/G#2 | Running hours [Generator] | hrs | Analog |  |  |  | 0.5 | GCP#2 | 1
|  | D/G#3 | Running hours [Generator] | hrs | Analog |  |  |  | 0.5 | GCP#3 | 1
|  | D/G#4 | Running hours [Generator] | hrs | Analog |  |  |  | 0.5 | GCP#4 | 1
145 |  | D/G#1 | Rack Reading | mm | Analog |  |  |  | 0.5 | GCP#1 | 1
|  | D/G#2 | Rack Reading | mm | Analog |  |  |  | 0.5 | GCP#2 | 1
|  | D/G#3 | Rack Reading | mm | Analog |  |  |  | 0.5 | GCP#3 | 1
|  | D/G#4 | Rack Reading | mm | Analog |  |  |  | 0.5 | GCP#4 | 1
146 |  | D/G#1 | Power [Generator] | kWe | Analog |  |  |  | 0.5 | GCP#1 | 1
|  | D/G#2 | Power [Generator] | kWe | Analog |  |  |  | 0.5 | GCP#2 | 1
|  | D/G#3 | Power [Generator] | kWe | Analog |  |  |  | 0.5 | GCP#3 | 1
|  | D/G#4 | Power [Generator] | kWe | Analog |  |  |  | 0.5 | GCP#4 | 1
147 |  | D/G#1 | Engine RPM | min-1 | Analog |  |  |  | 0.5 | GCP#1 | 1
|  | D/G#2 | Engine RPM | min-1 | Analog |  |  |  | 0.5 | GCP#2 | 1
|  | D/G#3 | Engine RPM | min-1 | Analog |  |  |  | 0.5 | GCP#3 | 1
|  | D/G#4 | Engine RPM | min-1 | Analog |  |  |  | 0.5 | GCP#4 | 1
148 |  | D/G#1 | Boost Air Pressure | Mpa | Analog |  |  |  | 0.5 | GCP#1 | 1
|  | D/G#2 | Boost Air Pressure | Mpa | Analog |  |  |  | 0.5 | GCP#2 | 1
|  | D/G#3 | Boost Air Pressure | Mpa | Analog |  |  |  | 0.5 | GCP#3 | 1
|  | D/G#4 | Boost Air Pressure | Mpa | Analog |  |  |  | 0.5 | GCP#4 | 1
149 |  | D/G#1 | Boost Air Temperature | °C | Analog |  |  |  | 0.5 | GCP#1 | 1
|  | D/G#2 | Boost Air Temperature | °C | Analog |  |  |  | 0.5 | GCP#2 | 1
|  | D/G#3 | Boost Air Temperature | °C | Analog |  |  |  | 0.5 | GCP#3 | 1
|  | D/G#4 | Boost Air Temperature | °C | Analog |  |  |  | 0.5 | GCP#4 | 1
150 |  | D/G#1 | F.O. Temperature | °C | Analog |  |  |  | 0.5 | GCP#1 | 1
|  | D/G#2 | F.O. Temperature | °C | Analog |  |  |  | 0.5 | GCP#2 | 1
|  | D/G#3 | F.O. Temperature | °C | Analog |  |  |  | 0.5 | GCP#3 | 1
|  | D/G#4 | F.O. Temperature | °C | Analog |  |  |  | 0.5 | GCP#4 | 1
151 |  | D/G#1 | F.O. Pressure | MPa | Analog |  |  |  | 0.5 | GCP#1 | 1
|  | D/G#2 | F.O. Pressure | MPa | Analog |  |  |  | 0.5 | GCP#2 | 1
|  | D/G#3 | F.O. Pressure | MPa | Analog |  |  |  | 0.5 | GCP#3 | 1
|  | D/G#4 | F.O. Pressure | MPa | Analog |  |  |  | 0.5 | GCP#4 | 1
152 |  | D/G#1 | Heavy Fault |  | Digital |  |  |  | 0.5 | GCP#1 | 1
|  | D/G#2 | Heavy Fault |  | Digital |  |  |  | 0.5 | GCP#2 | 1
|  | D/G#3 | Heavy Fault |  | Digital |  |  |  | 0.5 | GCP#3 | 1
|  | D/G#4 | Heavy Fault |  | Digital |  |  |  | 0.5 | GCP#4 | 1
153 |  | D/G#1 | Light Fault |  | Digital |  |  |  | 0.5 | GCP#1 | 1
|  | D/G#2 | Light Fault |  | Digital |  |  |  | 0.5 | GCP#2 | 1
|  | D/G#3 | Light Fault |  | Digital |  |  |  | 0.5 | GCP#3 | 1
|  | D/G#4 | Light Fault |  | Digital |  |  |  | 0.5 | GCP#4 | 1
154 |  | D/G#1 | Ready to start |  | Digital |  |  |  | 0.5 | GCP#1 | 1
|  | D/G#2 | Ready to start |  | Digital |  |  |  | 0.5 | GCP#2 | 1
|  | D/G#3 | Ready to start |  | Digital |  |  |  | 0.5 | GCP#3 | 1
|  | D/G#4 | Ready to start |  | Digital |  |  |  | 0.5 | GCP#4 | 1
155 | IM1 |  | No.1 Turning Motor | Abnormal trip | Digital |  |  |  |  | GCP#1 | 1
|  |  |  | FWD Running | Digital |  |  |  |  | GCP#1 | 1
|  |  |  | Rev Running | Digital |  |  |  |  | GCP#1 | 1
|  |  |  | Remote mode | Digital |  |  |  |  | GCP#1 | 1
|  |  | No.2 Turning Motor | Abnormal trip | Digital |  |  |  |  | GCP#2 | 1
|  |  |  | FWD Running | Digital |  |  |  |  | GCP#2 | 1
|  |  |  | Rev Running | Digital |  |  |  |  | GCP#2 | 1
|  |  |  | Remote mode | Digital |  |  |  |  | GCP#2 | 1
|  |  | No.3 Turning Motor | Abnormal trip | Digital |  |  |  |  | GCP#3 | 1
|  |  |  | FWD Running | Digital |  |  |  |  | GCP#3 | 1
|  |  |  | Rev Running | Digital |  |  |  |  | GCP#3 | 1
|  |  |  | Remote mode | Digital |  |  |  |  | GCP#3 | 1
|  |  | No.4 Turning Motor | Abnormal trip | Digital |  |  |  |  | GCP#4 | 1
|  |  |  | FWD Running | Digital |  |  |  |  | GCP#4 | 1
|  |  |  | Rev Running | Digital |  |  |  |  | GCP#4 | 1
|  |  |  | Remote mode | Digital |  |  |  |  | GCP#4 | 1
156 | IM2 |  | No.1 LO Priming Pump Motor status | Auto start [GCP] | Digital |  |  |  |  | GCP#1 | 1
|  |  |  | Auto Stop {GCP] | Digital |  |  |  |  | GCP#1 | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP#1 | 1
|  |  |  | Running | Digital |  |  |  |  | GCP#1 | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP#1 | 1
|  |  |  | Remote start [LCP] | Digital |  |  |  |  | GCP#1 | 1
|  |  |  | Remote Stop [LCP] | Digital |  |  |  |  | GCP#1 | 1
|  |  | No.2 LO Priming Pump Motor status | Auto start [GCP] | Digital |  |  |  |  | GCP#2 | 1
|  |  |  | Auto Stop {GCP] | Digital |  |  |  |  | GCP#2 | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP#2 | 1
|  |  |  | Running | Digital |  |  |  |  | GCP#2 | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP#2 | 1
|  |  |  | Remote start [LCP] | Digital |  |  |  |  | GCP#2 | 1
|  |  |  | Remote Stop [LCP] | Digital |  |  |  |  | GCP#2 | 1
|  |  | No.3 LO Priming Pump Motor status | Auto start [GCP] | Digital |  |  |  |  | GCP#3 | 1
|  |  |  | Auto Stop {GCP] | Digital |  |  |  |  | GCP#3 | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP#3 | 1
|  |  |  | Running | Digital |  |  |  |  | GCP#3 | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP#3 | 1
|  |  |  | Remote start [LCP] | Digital |  |  |  |  | GCP#3 | 1
|  |  |  | Remote Stop [LCP] | Digital |  |  |  |  | GCP#3 | 1
|  |  | No.4 LO Priming Pump Motor status | Auto start [GCP] | Digital |  |  |  |  | GCP#4 | 1
|  |  |  | Auto Stop {GCP] | Digital |  |  |  |  | GCP#4 | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP#4 | 1
|  |  |  | Running | Digital |  |  |  |  | GCP#4 | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP#4 | 1
|  |  |  | Remote start [LCP] | Digital |  |  |  |  | GCP#4 | 1
|  |  |  | Remote Stop [LCP] | Digital |  |  |  |  | GCP#4 | 1
157 | IM3 |  | No.1 Air Compressor status | Auto start [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
|  |  | No.2 Air Compressor status | Auto start [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
158 | IM4 |  | No.1 Mist Fan | Auto start [GCP] | Digital |  |  |  |  | GCP#1 | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP#1 | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP#1 | 1
|  |  |  | Running | Digital |  |  |  |  | GCP#1 | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP#1 | 1
|  |  | No.2 Mist Fan | Auto start [GCP] | Digital |  |  |  |  | GCP#2 | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP#2 | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP#2 | 1
|  |  |  | Running | Digital |  |  |  |  | GCP#2 | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP#2 | 1
|  |  | No.3 Mist Fan | Auto start [GCP] | Digital |  |  |  |  | GCP#3 | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP#3 | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP#3 | 1
|  |  |  | Running | Digital |  |  |  |  | GCP#3 | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP#3 | 1
|  |  | No.4 Mist Fan | Auto start [GCP] | Digital |  |  |  |  | GCP#4 | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP#4 | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP#4 | 1
|  |  |  | Running | Digital |  |  |  |  | GCP#4 | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP#4 | 1
159 | IM5 |  | No.1 DO Transfer Pump | Auto start [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
|  |  | No.2 DO Transfer Pump | Auto start [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
160 | IM6 |  | No.1 DO Feed Pump | Auto start [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
|  |  | No.2 DO Feed Pump | Auto start [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
161 | IM7 |  | No.1 HO Transfer Pump | Auto start [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
|  |  | No.2 HO Transfer Pump | Auto start [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
162 | IM8 |  | No.1 HO Pressure Pump | Auto start [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
|  |  | No.2 HO Pressure Pump | Auto start [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
163 | IM9 |  | No.1 HO Feed Pump | Auto start [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
|  |  | No.2 HO Feed Pump | Auto start [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
164 | IM10 |  | No.1 FO Drain Pump | Auto start [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
|  |  | No.2 FO Drain Pump | Auto start [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
165 | IM11 |  | No.1 DO/HO change over valve [Engine inlet] | Energize | Digital |  |  |  |  | GCP#1 | 1
|  |  |  | De-energize | Digital |  |  |  |  | GCP#1 | 1
|  |  | No.2 DO/HO change over valve [Engine inlet] | Energize | Digital |  |  |  |  | GCP#2 | 1
|  |  |  | De-energize | Digital |  |  |  |  | GCP#2 | 1
|  |  | No.3 DO/HO change over valve [Engine inlet] | Energize | Digital |  |  |  |  | GCP#3 | 1
|  |  |  | De-energize | Digital |  |  |  |  | GCP#3 | 1
|  |  | No.4 DO/HO change over valve [Engine inlet] | Energize | Digital |  |  |  |  | GCP#4 | 1
|  |  |  | De-energize | Digital |  |  |  |  | GCP#4 | 1
|  |  | No.1 DO/HO change over valve [Engine outlet] | Energize | Digital |  |  |  |  | GCP#1 | 1
|  |  |  | De-energize | Digital |  |  |  |  | GCP#1 | 1
|  |  | No.2 DO/HO change over valve [Engine outlet] | Energize | Digital |  |  |  |  | GCP#2 | 1
|  |  |  | De-energize | Digital |  |  |  |  | GCP#2 | 1
|  |  | No.3 DO/HO change over valve [Engine outlet] | Energize | Digital |  |  |  |  | GCP#3 | 1
|  |  |  | De-energize | Digital |  |  |  |  | GCP#3 | 1
|  |  | No.4 DO/HO change over valve [Engine outlet] | Energize | Digital |  |  |  |  | GCP#4 | 1
|  |  |  | De-energize | Digital |  |  |  |  | GCP#4 | 1
166 | IM12 |  | No.1 Inlet Fan | Auto start [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
|  |  | No.2 Inlet Fan | Auto start [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
|  |  | No.3 Inlet Fan | Auto start [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
|  |  | No.4 Inlet Fan | Auto start [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
|  |  | No.5 Inlet Fan | Auto start [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
167 | IM13 |  | No.1 Outlet Fan | Auto start [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
|  |  | No.2 Outlet Fan | Auto start [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
|  |  | No.3 Outlet Fan | Auto start [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
|  |  | No.4 Outlet Fan | Auto start [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
|  |  | No.5 Outlet Fan | Auto start [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
168 | IM14 |  | Overhead crane | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
169 | IM15 |  | Air conditioner | Fault | Digital |  |  |  |  | GCP | 1
170 | IM16 |  | Viscosity controller | Fault | Digital |  |  |  |  | GCP | 1
171 | IM29 |  | L.O makeup Pump | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
172 | IM19 |  | No.1 Alternator Space heater | Auto start [GCP] | Digital |  |  |  |  | GCP#1 | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP#1 | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP#1 | 1
|  |  |  | Running | Digital |  |  |  |  | GCP#1 | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP#1 | 1
|  |  | No.2 Alternator Space heater | Auto start [GCP] | Digital |  |  |  |  | GCP#2 | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP#2 | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP#2 | 1
|  |  |  | Running | Digital |  |  |  |  | GCP#2 | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP#2 | 1
|  |  | No.3 Alternator Space heater | Auto start [GCP] | Digital |  |  |  |  | GCP#3 | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP#3 | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP#3 | 1
|  |  |  | Running | Digital |  |  |  |  | GCP#3 | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP#3 | 1
|  |  | No.4 Alternator Space heater | Auto start [GCP] | Digital |  |  |  |  | GCP#4 | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP#4 | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP#4 | 1
|  |  |  | Running | Digital |  |  |  |  | GCP#4 | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP#4 | 1
173 | IM39 |  | DO unloading pump | Abnormal trip | Digital |  |  |  |  | GCP | 1 |  | LCBD: Start, Stop Push button [manual]
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
174 | IM 22 |  | HO unloading pump | Abnormal trip | Digital |  |  |  |  | GCP | 1 |  | LCBH: Start, Stop Push button [manual]
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
175 | IM18 |  | Inline heater | Auto start [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
176 | IM23 |  | HO settling tank heater | Auto start [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
177 | IM24 |  | No.1 HO purifier Heater | Fault | Digital |  |  |  |  | GCP | 1
|  |  | No.2 HO purifier Heater | Fault | Digital |  |  |  |  | GCP | 1
178 | IM25 |  | No.1 HO purifier Pump | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  | No.1 HO purifier Pump | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
179 | IM27 |  | No.1 HO service tank heater | Auto start [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
|  |  | No.2 HO service tank heater | Auto start [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
180 | IM17 |  | HO line heater | Fault | Digital |  |  |  |  | GCP | 1
181 | IM28 |  | HO back wash filter | Fault | Digital |  |  |  |  | GCP | 1
182 | IM30 |  | No.1 F.O drain tank heater | Auto start [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
|  |  | No.2 F.O drain tank heater | Auto start [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
183 | IM26 |  | No.1 HT Radiator fan motor | Auto start [GCP] | Digital |  |  |  |  | GCP#1 | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP#1 | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP#1 | 1
|  |  |  | Running | Digital |  |  |  |  | GCP#1 | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP#1 | 1
|  |  | No.2 HT Radiator fan motor | Auto start [GCP] | Digital |  |  |  |  | GCP#2 | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP#2 | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP#2 | 1
|  |  |  | Running | Digital |  |  |  |  | GCP#2 | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP#2 | 1
|  |  | No.3 HT Radiator fan motor | Auto start [GCP] | Digital |  |  |  |  | GCP#3 | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP#3 | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP#3 | 1
|  |  |  | Running | Digital |  |  |  |  | GCP#3 | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP#3 | 1
|  |  | No.4 HT Radiator fan motor | Auto start [GCP] | Digital |  |  |  |  | GCP#4 | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP#4 | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP#4 | 1
|  |  |  | Running | Digital |  |  |  |  | GCP#4 | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP#4 | 1
184 | IM38 |  | No.1 LT Radiator fan motor | Auto start [GCP] | Digital |  |  |  |  | GCP#1 | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP#1 | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP#1 | 1
|  |  |  | Running | Digital |  |  |  |  | GCP#1 | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP#1 | 1
|  |  | No.2 LT Radiator fan motor | Auto start [GCP] | Digital |  |  |  |  | GCP#2 | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP#2 | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP#2 | 1
|  |  |  | Running | Digital |  |  |  |  | GCP#2 | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP#2 | 1
|  |  | No.3 LT Radiator fan motor | Auto start [GCP] | Digital |  |  |  |  | GCP#3 | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP#3 | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP#3 | 1
|  |  |  | Running | Digital |  |  |  |  | GCP#3 | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP#3 | 1
|  |  | No.4 LT Radiator fan motor | Auto start [GCP] | Digital |  |  |  |  | GCP#4 | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP#4 | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP#4 | 1
|  |  |  | Running | Digital |  |  |  |  | GCP#4 | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP#4 | 1
185 | IM31 |  | Drain discharge pump | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
186 | IM32 |  | Make up water pump | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
187 | IM20 |  | No.1 LO purifier heater | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  | No.2 LO purifier heater | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  | No.3 LO purifier heater | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  | No.4 LO purifier heater | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
188 | IM21 |  | No.1 LO purifier pump | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  | No.2 LO purifier pump | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  | No.3 LO purifier pump | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  | No.4 LO purifier pump | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
189 | IM34 |  | Sludge transfer pump No.1 | Auto start [GCP] | Digital |  |  |  |  | GCP | 1 |  | LCBS: Start, Stop Push button [manual]
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
|  |  | Sludge transfer pump No.2 | Auto start [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  |  |  |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  |  | Auto mode | Digital |  |  |  |  | GCP | 1
190 | IM35 |  | No.1 Oily water drain pump | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
|  |  | No.2 Oily water drain pump | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
191 | IM33 |  | Water supply pump | Abnormal trip | Digital |  |  |  |  | GCP | 1
|  |  |  | Running | Digital |  |  |  |  | GCP | 1
192 | IM37 |  | Lighting for Engine room | Fault | Digital |  |  |  |  | GCP | 1
193 |  |  | Control Panel | Fault | Digital |  |  |  |  | GCP | 1
194 |  |  | No.1 OMD | Fault | Digital |  |  |  |  | GCP | 1
|  |  | No.2 OMD | Fault | Digital |  |  |  |  | GCP | 1
|  |  | No.3 OMD | Fault | Digital |  |  |  |  | GCP | 1
|  |  | No.4 OMD | Fault | Digital |  |  |  |  | GCP | 1
195 |  |  | Heat trace No.1 | Fault | Digital |  |  |  |  | GCP | 1
|  |  | Heat trace No.2 | Fault | Digital |  |  |  |  | GCP | 1
|  |  | Heat trace No.3 | Fault | Digital |  |  |  |  | GCP | 1
|  |  | Heat trace No.4 | Fault | Digital |  |  |  |  | GCP | 1
|  |  | Heat trace No.5 | Fault | Digital |  |  |  |  | GCP | 1
|  |  | Heat trace No.6 | Fault | Digital |  |  |  |  | GCP | 1
|  |  | Heat trace No.7 | Fault | Digital |  |  |  |  | GCP | 1
|  |  | Heat trace No.8 | Fault | Digital |  |  |  |  | GCP | 1
|  |  | Heat trace No.9 | Fault | Digital |  |  |  |  | GCP | 1
|  |  | Heat trace No.10 | Fault | Digital |  |  |  |  | GCP | 1
|  |  | Heat trace No.11 | Fault | Digital |  |  |  |  | GCP | 1
|  |  | Heat trace No.12 | Fault | Digital |  |  |  |  | GCP | 1
|  |  | Heat trace No.13 | Fault | Digital |  |  |  |  | GCP | 1
|  |  | Heat trace No.14 | Fault | Digital |  |  |  |  | GCP | 1
|  |  | Heat trace No.15 | Fault | Digital |  |  |  |  | GCP | 1
|  |  | Heat trace No.16 | Fault | Digital |  |  |  |  | GCP | 1
|  |  | Heat trace No.17 | Fault | Digital |  |  |  |  | GCP | 1
|  |  | Heat trace No.18 | Fault | Digital |  |  |  |  | GCP | 1
|  |  | Heat trace No.19 | Fault | Digital |  |  |  |  | GCP | 1
|  |  | Heat trace No.20 | Fault | Digital |  |  |  |  | GCP | 1
|  |  | Heat trace No.21 | Fault | Digital |  |  |  |  | GCP | 1
|  |  | Heat trace No.22 | Fault | Digital |  |  |  |  | GCP | 1
|  |  | Heat trace No.23 | Fault | Digital |  |  |  |  | GCP | 1
|  |  | Heat trace No.24 | Fault | Digital |  |  |  |  | GCP | 1
196 |  |  | Drums | Fault | Digital |  |  |  |  | GCP | 1
197 | 50,51 | D/G#1 | Over Current(LTD,STD,INST) | [5 empty] | 0.5 | GCP#1 | 1
| 50,51 | D/G#2 | Over Current(LTD,STD,INST) | [5 empty] | 0.5 | GCP#2 | 1
| 50,51 | D/G#3 | Over Current(LTD,STD,INST) | [5 empty] | 0.5 | GCP#3 | 1
| 50,51 | D/G#4 | Over Current(LTD,STD,INST) | [5 empty] | 0.5 | GCP#4 | 1
202 | 59 | D/G#1 | Over Voltage | [5 empty] | 0.5 | GCP#1 | 1
| 59 | D/G#2 | Over Voltage | [5 empty] | 0.5 | GCP#2 | 1
| 59 | D/G#3 | Over Voltage | [5 empty] | 0.5 | GCP#3 | 1
| 59 | D/G#4 | Over Voltage | [5 empty] | 0.5 | GCP#4 | 1
203 | 51N | D/G#1 | Earth Fault | [5 empty] | 0.5 | GCP#1 | 1
| 51N | D/G#2 | Earth Fault | [5 empty] | 0.5 | GCP#2 | 1
| 51N | D/G#3 | Earth Fault | [5 empty] | 0.5 | GCP#3 | 1
| 51N | D/G#4 | Earth Fault | [5 empty] | 0.5 | GCP#4 | 1
204 | 27 | D/G#1 | Under Voltage | [5 empty] | 0.5 | GCP#1 | 1
| 27 | D/G#2 | Under Voltage | [5 empty] | 0.5 | GCP#2 | 1
| 27 | D/G#3 | Under Voltage | [5 empty] | 0.5 | GCP#3 | 1
| 27 | D/G#4 | Under Voltage | [5 empty] | 0.5 | GCP#4 | 1
205 | 87G | D/G#1 | Diff Protection | [5 empty] | 0.5 | GCP#1 | 1
| 87G | D/G#2 | Diff Protection | [5 empty] | 0.5 | GCP#2 | 1
| 87G | D/G#3 | Diff Protection | [5 empty] | 0.5 | GCP#3 | 1
| 87G | D/G#4 | Diff Protection | [5 empty] | 0.5 | GCP#4 | 1
206 | 40 | D/G#1 | Under Excitation | [5 empty] | 0.5 | GCP#1 | 1
| 40 | D/G#2 | Under Excitation | [5 empty] | 0.5 | GCP#2 | 1
| 40 | D/G#3 | Under Excitation | [5 empty] | 0.5 | GCP#3 | 1
| 40 | D/G#4 | Under Excitation | [5 empty] | 0.5 | GCP#4 | 1
207 | 32R | D/G#1 | Reverse Power | [5 empty] | 0.5 | GCP#1 | 1
| 32R | D/G#2 | Reverse Power | [5 empty] | 0.5 | GCP#2 | 1
| 32R | D/G#3 | Reverse Power | [5 empty] | 0.5 | GCP#3 | 1
| 32R | D/G#4 | Reverse Power | [5 empty] | 0.5 | GCP#4 | 1
208 | 81 | D/G#1 | Frequency | [5 empty] | 0.5 | GCP#1 | 1
| 81 | D/G#2 | Frequency | [5 empty] | 0.5 | GCP#2 | 1
| 81 | D/G#3 | Frequency | [5 empty] | 0.5 | GCP#3 | 1
| 81 | D/G#4 | Frequency | [5 empty] | 0.5 | GCP#4 | 1
209 | 46 | D/G#1 | Negative Over Current | [5 empty] | 0.5 | GCP#1 | 1
| 46 | D/G#2 | Negative Over Current | [5 empty] | 0.5 | GCP#2 | 1
| 46 | D/G#3 | Negative Over Current | [5 empty] | 0.5 | GCP#3 | 1
| 46 | D/G#4 | Negative Over Current | [5 empty] | 0.5 | GCP#4 | 1
210 | 86 | D/G#1 | Lockout | [5 empty] | 0.5 | GCP#1 | 1
| 86 | D/G#2 | Lockout | [5 empty] | 0.5 | GCP#2 | 1
| 86 | D/G#3 | Lockout | [5 empty] | 0.5 | GCP#3 | 1
| 86 | D/G#4 | Lockout | [5 empty] | 0.5 | GCP#4 | 1
211 | 50,51 |  | Over Current(LTD,STD,INST) | [6 empty] | GCP | 1 |  | Step up feeder
212 | 50,51 |  | Over Current(LTD,STD,INST) | [6 empty] | GCP | 1 |  | Step down feeder
213 | 51N |  | Over Current | [6 empty] | GCP | 1 |  | NGR
214 | 5E | D/G#1 | Emergency stop local box |  | Digital |  |  |  | 0.5 | Gen Local Box#1 | 1
| 5E | D/G#2 | Emergency stop local box |  | Digital |  |  |  | 0.5 | Gen Local Box#2 | 1
| 5E | D/G#3 | Emergency stop local box |  | Digital |  |  |  | 0.5 | Gen Local Box#3 | 1
| 5E | D/G#4 | Emergency stop local box |  | Digital |  |  |  | 0.5 | Gen Local Box#4 | 1
Note on D358: ====== ID#AAAB5FvnHfw 佐々木 亮 (2026-04-30 03:06:20) No need. Spare for 1B to 3B
Note on D664: ====== ID#AAAB5FvnHfs 佐々木 亮 (2026-04-30 03:06:20) We don’t have this sensor
Note on D679: ====== ID#AAAB5FvnHfo 佐々木 亮 (2026-04-30 03:06:20) Same signal as No.100 [PTIA]
Note on D684: ====== ID#AAAB5FvnHfg 佐々木 亮 (2026-04-30 03:06:20) No Air Temp. sensor
Note on D689: ====== ID#AAAB5FvnHf4 佐々木 亮 (2026-04-30 03:06:20) Use following sensor; No.125[TRDI]、No.127[TRHI]
Note on D694: ====== ID#AAAB5FvnHfk 佐々木 亮 (2026-04-30 03:06:20) Same singal as No.95[PTFO]
Note on D699: ====== ID#AAAB5FvnHfY 佐々木 亮 (2026-04-30 03:06:20) Not necessary
Note on D704: ====== ID#AAAB5FvnHfc 佐々木 亮 (2026-04-30 03:06:20) Not necessary
Note on D1129: ====== ID#AAAB5FvnHf0 佐々木 亮 (2026-04-30 03:06:20) What is this?

## Modbus Digital
Name | Address
Pump 1 | 10001
Pump 2 | 10002
Pump 3 | 10003
Pump 4 | 10004
Pump 5 | 10005
Pump 6 | 10006
Pump 7 | 10007
Pump 8 | 10008
Pump 9 | 10009
Pump 10 | 10010
Pump 11 | 10011
Pump 12 | 10012
LC_D.O.service.tank | 10013
LC_H.O.settling.tank | 10014
LH_D.O.service.tank | 10015
LH_F.O. drain tank | 10016
LH_H.O.settling.tank | 10017
LL_D.O.service.tank | 10018
LL_F.O. drain tank | 10019
LL_H.O.service.tank | 10020
LL_H.O.settling.tank | 10021
LS_Sludge.tank | 10022
TS_D.O.service.tank | 10023
TS_F.O. drain tank | 10024
TS_H.O.purifier.No1 | 10025
TS_H.O.purifier.No2 | 10026
TS_H.O.purifier.No3 | 10027
TS_H.O.settling.tank | 10028
TS1_H.O.service.tank | 10029
TS2_H.O.service.tank | 10030
TSH_D.O.service.tank | 10031
TSH_F.O. drain tank | 10032
TSH_H.O.service.tank | 10033
TSH_H.O.settling.tank | 10034